## 16-17
Date Stamp | .Gear Island 1050 Fluoride | .Gear Island 1050 Fluoride Analyser #2 | .Te Marua PS Fluoride Residual | .Te Marua TP Fluoride Residual | .Wainui Fluoride Building Fluoride Residual Stream 1 | .Wainui Fluoride Building Fluoride Residual Stream 2 | .Waterloo Naenae Fluoride Residual
2016-07-01 23:00 | 0.68409 | 0 | 0 | 0 | 0 | 0 | 0.84908
2016-07-02 23:00 | 0.54054 | 0 | 0 | 0 | 0 | 0 | 0.83454
2016-07-03 23:00 | 0.52581 | 0 | 0 | 0 | 0 | 0 | 0.85124 |  |  | Analysers not installed or was off
2016-07-04 23:00 | 0.60781 | 0 | 0 | 0 | 0 | 0 | 0.8672 |  |  | Fluoride not dosed
2016-07-05 23:00 | 0.56695 | 0 | 0 | 0 | 0 | 0 | 0.83851 |  |  | fluoride dosed but outside recommended range
2016-07-06 23:00 | 0.61203 | 0 | 0 | 0 | 0 | 0 | 0.82831 |  |  | Fluoride dosed but within recommended range
2016-07-07 23:00 | 0.90275 | 0 | 0 | 0 | 0 | 0 | 0.85698
2016-07-08 23:00 | 0.92557 | 0 | 0 | 0 | 0 | 0 | 0.83216 |  | Assumptions: |  | 1. Values less than 0.1 indicates that fluoride is not being dosed
2016-07-09 23:00 | 0.90989 | 0 | 0 | 0 | 0 | 0 | 0.85032 |  |  |  | 2. The Gear Island sampling point is downstream of the plant and can contain a residual from the Wainuiomata WTP
2016-07-10 23:00 | 0.92035 | 0 | 0 | 0 | 0 | 0 | 0.83833
2016-07-11 23:00 | 0.89716 | 0 | 0 | 0 | 0.21788 | 0.19957 | 0.85073
2016-07-12 23:00 | 0.90953 | 0 | 0 | 0 | 0.75768 | 0.71749 | 0.87586
2016-07-13 23:00 | 0.91483 | 0 | 0 | 0 | 0.4291 | 0.41735 | 0.90175
2016-07-14 23:00 | 0.71956 | 0 | 0 | 0 | 0.35129 | 0.34482 | 0.91013
2016-07-15 23:00 | 0.26186 | 0 | 0 | 0 | 0.75076 | 0.7391 | 0.91817
2016-07-16 23:00 | 0.2976 | 0 | 0 | 0 | 0.51183 | 0.51425 | 0.86838
2016-07-17 23:00 | 0.089469 | 0 | 0 | 0 | 0.051706 | 0.059673 | 0.88343
2016-07-18 23:00 | 0.22251 | 0 | 0 | 0 | 0.050136 | 0.05608 | 0.87056
2016-07-19 23:00 | 0.82447 | 0 | 0 | 0 | 0.051522 | 0.05626 | 0.89107
2016-07-20 23:00 | 0.75273 | 0 | 0 | 0 | 0.54816 | 0.56836 | 0.88165
2016-07-21 23:00 | 1.0116 | 0 | 0 | 0 | 0.35981 | 0.41805 | 0.86164
2016-07-22 23:00 | 0.99955 | 0 | 0 | 0 | 0.88015 | 1.021 | 0.90789
2016-07-23 23:00 | 1.0273 | 0 | 0 | 0 | 0.73929 | 0.82111 | 0.89673
2016-07-24 23:00 | 0.93868 | 0 | 0 | 0 | 0.8588 | 0.95748 | 0.87694
2016-07-25 23:00 | 0.99851 | 0 | 0 | 0 | 0.76625 | 0.87128 | 0.887
2016-07-26 23:00 | 0.97271 | 0 | 0 | 0 | 0.33138 | 0.37897 | 0.89512
2016-07-27 23:00 | 0.87183 | 0 | 0 | 0 | 0.71857 | 0.80088 | 0.9122
2016-07-28 23:00 | 1.0058 | 0 | 0 | 0 | 0.90188 | 0.91493 | 0.42309
2016-07-29 23:00 | 0.99791 | 0 | 0 | 0 | 0.90116 | 0.86634 | 0.065022
2016-07-30 23:00 | 1.005 | 0 | 0 | 0 | 0.89365 | 0.86133 | 0.080643
2016-07-31 23:00 | 0.99038 | 0 | 0 | 0 | 0.88343 | 0.86626 | 0.37153
2016-08-01 23:00 | 0.74364 | 0 | 0 | 0 | 0.063967 | 0.067676 | 0.88016
2016-08-02 23:00 | 0.86204 | 0 | 0 | 0 | 0.50198 | 0.49161 | 0.8889
2016-08-03 23:00 | 1.0114 | 0 | 0 | 0 | 0.17987 | 0.17715 | 0.90224
2016-08-04 23:00 | 0.76698 | 0 | 0 | 0 | 0.43537 | 0.43619 | 0.88647
2016-08-05 23:00 | 0.95362 | 0 | 0 | 0 | 0.26388 | 0.26444 | 0.87116
2016-08-06 23:00 | 0.96031 | 0 | 0 | 0 | 0.29103 | 0.28621 | 0.86553
2016-08-07 23:00 | 0.96225 | 0 | 0 | 0 | 0.26734 | 0.26073 | 0.8726
2016-08-08 23:00 | 0.97339 | 0 | 0 | 0 | 0.26569 | 0.25528 | 0.8475
2016-08-09 23:00 | 0.88325 | 0 | 0 | 0 | 0.21575 | 0.20702 | 0.89375
2016-08-10 23:00 | 0.60414 | 0 | 0 | 0 | 0.56528 | 0.5354 | 0.84808
2016-08-11 23:00 | 0.93384 | 0 | 0 | 0 | 0.8835 | 0.8298 | 0.82282
2016-08-12 23:00 | 0.94948 | 0 | 0 | 0 | 0.30175 | 0.28569 | 0.81168
2016-08-13 23:00 | 0.94401 | 0 | 0 | 0 | 0.10112 | 0.10145 | 0.81904
2016-08-14 23:00 | 0.8681 | 0 | 0 | 0 | 0.40881 | 0.39063 | 0.85238
2016-08-15 23:00 | 0.92274 | 0 | 0 | 0 | 0.88673 | 0.82037 | 0.86779
2016-08-16 23:00 | 0.93059 | 0 | 0 | 0 | 0.76059 | 0.67835 | 0.87324
2016-08-17 23:00 | 0.95171 | 0 | 0 | 0 | 0.17688 | 0.15825 | 0.76803
2016-08-18 23:00 | 0.93417 | 0 | 0 | 0 | 0.26793 | 0.24504 | 0.846
2016-08-19 23:00 | 0.93212 | 0 | 0 | 0 | 0.32265 | 0.29599 | 0.83382
2016-08-20 23:00 | 0.92615 | 0 | 0 | 0 | 0.3096 | 0.28702 | 0.84987
2016-08-21 23:00 | 0.91611 | 0 | 0 | 0 | 0.28648 | 0.26842 | 0.7968
2016-08-22 23:00 | 0.81954 | 0 | 0 | 0 | 0.45315 | 0.42425 | 0.81754
2016-08-23 23:00 | 0.90852 | 0 | 0 | 0 | 0.8815 | 0.82666 | 0.81938
2016-08-24 23:00 | 0.91766 | 0 | 0 | 0 | 0.88554 | 0.8321 | 0.85823
2016-08-25 23:00 | 0.78562 | 0 | 0 | 0 | 0.88118 | 0.82041 | 0.84496
2016-08-26 23:00 | 0.92541 | 0 | 0 | 0 | 0.88061 | 0.82363 | 0.82602
2016-08-27 23:00 | 0.90159 | 0 | 0 | 0 | 0.86936 | 0.81199 | 0.84489
2016-08-28 23:00 | 0.91594 | 0 | 0 | 0 | 0.79664 | 0.74139 | 0.84387
2016-08-29 23:00 | 0.90773 | 0 | 0 | 0 | 0.86514 | 0.81794 | 0.84664
2016-08-30 23:00 | 0.91939 | 0 | 0 | 0 | 0.86986 | 0.82 | 0.77677
2016-08-31 23:00 | 0.90864 | 0 | 0 | 0 | 0.86627 | 0.81587 | 0.65293
2016-09-01 23:00 | 0.92662 | 0 | 0 | 0 | 0.73829 | 0.68236 | 0.8179
2016-09-02 23:00 | 0.89983 | 0 | 0 | 0 | 0.52905 | 0.48614 | 0.84431
2016-09-03 23:00 | 0.96004 | 0 | 0 | 0 | 0.86191 | 0.79284 | 0.85039
2016-09-04 23:00 | 0.96839 | 0 | 0 | 0 | 0.83602 | 0.75995 | 0.84192
2016-09-05 23:00 | 0.96959 | 0 | 0 | 0 | 0.86259 | 0.78239 | 0.82689
2016-09-06 23:00 | 0.96672 | 0 | 0 | 0 | 0.49782 | 0.45212 | 0.83183
2016-09-07 23:00 | 0.75381 | 0 | 0 | 0 | 0.3061 | 0.16656 | 0.81418
2016-09-08 23:00 | 0.79697 | 0 | 0 | 0 | 0.38288 | 0.02005 | 0.8642
2016-09-09 23:00 | 0.86801 | 0 | 0 | 0 | 0.8318 | 0.036973 | 0.87303
2016-09-10 23:00 | 0.96359 | 0 | 0 | 0 | 0.82853 | 0.071516 | 0.85205
2016-09-11 23:00 | 0.97839 | 0 | 0 | 0 | 0.83462 | 0.12205 | 0.85232
2016-09-12 23:00 | 0.87684 | 0 | 0 | 0 | 0.58609 | 0.28841 | 0.84403
2016-09-13 23:00 | 0.35235 | 0 | 0 | 0 | 0.051405 | 0.14228 | 0.83531
2016-09-14 23:00 | 0.67454 | 0 | 0 | 0 | 0.50795 | 0.49157 | 0.85234
2016-09-15 23:00 | 0.88727 | 0 | 0 | 0 | 0.72899 | 0.56434 | 0.80152
2016-09-16 23:00 | 0.13657 | 0 | 0 | 0 | 0.088057 | 0.064613 | 0.83535
2016-09-17 23:00 | 0.089981 | 0 | 0 | 0 | 0.17232 | 0.13944 | 0.82
2016-09-18 23:00 | 0.54109 | 0 | 0 | 0 | 0.13979 | 0.11886 | 0.85533
2016-09-19 23:00 | 0.78567 | 0 | 0 | 0 | 0.14984 | 0.12973 | 0.80598
2016-09-20 23:00 | 0.56477 | 0 | 0 | 0 | 0.15831 | 0.13698 | 0.82826
2016-09-21 23:00 | 0.82286 | 0 | 0 | 0 | 0.16188 | 0.14596 | 0.84353
2016-09-22 23:00 | 0.82502 | 0 | 0 | 0 | 0.12473 | 0.12692 | 0.81252
2016-09-23 23:00 | 0.81957 | 0 | 0 | 0 | 0.1417 | 0.16821 | 0.81469
2016-09-24 23:00 | 0.78841 | 0 | 0 | 0 | 0.83318 | 0.80895 | 0.85307
2016-09-26 | 0.84465 | 0 | 0 | 0 | 0.84054 | 0.72412 | 0.83214
2016-09-27 | 0.81942 | 0 | 0 | 0 | 0.78106 | 0.65167 | 0.84773
2016-09-28 | 0.75133 | 0 | 0 | 0 | 0.72992 | 0.61382 | 0.85767
2016-09-29 | 0.76947 | 0 | 0 | 0 | 0.77939 | 0.63398 | 0.85866
2016-09-30 | 0.81683 | 0 | 0 | 0 | 0.85094 | 0.67729 | 0.85859
2016-10-01 | 0.77358 | 0 | 0 | 0 | 0.67919 | 0.54841 | 0.84284
2016-10-02 | 0.83458 | 0 | 0 | 0 | 0.86414 | 0.69125 | 0.84474
2016-10-03 | 0.81241 | 0 | 0 | 0 | 0.7846 | 0.64319 | 0.84884
2016-10-04 | 0.81627 | 0 | 0 | 0 | 0.87714 | 0.7249 | 0.86562
2016-10-05 | 0.63488 | 0 | 0 | 0 | 0.87378 | 0.72292 | 0.54144
2016-10-06 | 0.39994 | 0 | 0 | 0 | 0.87003 | 0.72085 | 0.07826
2016-10-07 | 0.47023 | 0 | 0 | 0 | 0.84613 | 0.77083 | 0.48684
2016-10-08 | 0.33174 | 0 | 0 | 0 | 0.76455 | 0.81233 | 0.82211
2016-10-09 | 0.32981 | 0 | 0 | 0 | 0.87276 | 0.91656 | 0.82115
2016-10-10 | 0.56617 | 0 | 0 | 0 | 0.66357 | 1.1258 | 0.83085
2016-10-11 | 0.55394 | 0 | 0 | 0 | 0.072695 | 0.84539 | 0.84303
2016-10-12 | 0.64153 | 0 | 0 | 0 | 0.27182 | 0.10735 | 0.84424
2016-10-13 | 0.64469 | 0 | 0 | 0 | 0.3544 | 0.17601 | 0.82996
2016-10-14 | 0.55431 | 0 | 0 | 0 | 0.58685 | 0.57345 | 0.8072
2016-10-15 | 0.74759 | 0 | 0 | 0 | 0.51579 | 0.45298 | 0.81974
2016-10-16 | 0.65286 | 0 | 0 | 0 | 0.41978 | 0.38763 | 0.81986
2016-10-17 | 0.74938 | 0 | 0 | 0 | 0.84506 | 0.72743 | 0.8285
2016-10-18 | 0.76562 | 0 | 0 | 0 | 0.84945 | 0.67701 | 0.82084
2016-10-19 | 0.80915 | 0 | 0 | 0 | 0.80149 | 0.65295 | 0.8129
2016-10-20 | 0.78173 | 0 | 0 | 0 | 0.88352 | 0.70624 | 0.82919
2016-10-21 | 0.79348 | 0 | 0 | 0 | 0.865 | 0.66418 | 0.80956
2016-10-22 | 0.76385 | 0 | 0 | 0 | 0.83553 | 0.63037 | 0.81695
2016-10-23 | 0.75332 | 0 | 0 | 0 | 0.83041 | 0.61882 | 0.8291
2016-10-24 | 0.75971 | 0 | 0 | 0 | 0.83981 | 0.60739 | 0.80329
2016-10-25 | 0.76862 | 0 | 0 | 0 | 0.80842 | 0.57266 | 0.82003
2016-10-26 | 0.71727 | 0 | 0 | 0 | 0.4196 | 0.31312 | 0.75438
2016-10-27 | 0.70175 | 0 | 0 | 0 | 0.082812 | 0.073317 | 0.83484
2016-10-28 | 0.64252 | 0 | 0 | 0 | 0.12553 | 0.13082 | 0.806
2016-10-29 | 0.53522 | 0 | 0 | 0 | 0.05019 | 0 | 0.47219
2016-10-30 | 0.47022 | 0 | 0 | 0 | 0.050061 | 0 | 0.073459
2016-10-31 | 0.56283 | 0 | 0 | 0 | 0.5136 | 0.36497 | 0.56966
2016-11-01 | 0.75897 | 0 | 0 | 0 | 0.894 | 0.47459 | 0.78665
2016-11-02 | 0.76663 | 0 | 0 | 0 | 0.88916 | 0.39421 | 0.81687
2016-11-03 | 0.81518 | 0 | 0 | 0 | 0.89088 | 0.37404 | 0.77092
2016-11-04 | 0.77992 | 0 | 0 | 0 | 0.89712 | 0.34412 | 0.83278
2016-11-05 | 0.77056 | 0 | 0 | 0 | 0.89372 | 0.32647 | 0.80844
2016-11-06 | 0.77304 | 0 | 0 | 0 | 0.89662 | 0.31123 | 0.81068
2016-11-07 | 0.76083 | 0 | 0 | 0 | 0.79763 | 0.27263 | 0.50794
2016-11-08 | 0.70162 | 0 | 0 | 0 | 0.14934 | 0.048826 | 0.080148
2016-11-09 | 0.65792 | 0 | 0 | 0 | 0.55576 | 0.371 | 0.56829
2016-11-10 | 0.72308 | 0 | 0 | 0 | 0.59902 | 0.56529 | 0.83112
2016-11-11 | 0.68366 | 0 | 0 | 0 | 0.19986 | 0.20081 | 0.8326
2016-11-12 | 0.69909 | 0 | 0 | 0 | 0.20901 | 0.2311 | 0.83658
2016-11-13 | 0.67648 | 0 | 0 | 0 | 0.1694 | 0.19766 | 0.822
2016-11-14 | 0.10691 | 0 | 0 | 0 | 0.083414 | 0.10077 | 0.52371
2016-11-15 | 0.28843 | 0 | 0 | 0 | 0.067261 | 0.12656 | 0.086849
2016-11-16 | 0.67402 | 0 | 0 | 0 | 0.11236 | 0.23936 | 0.52896
2016-11-17 | 0.68087 | 0 | 0 | 0 | 0.075328 | 0.21973 | 0.85804
2016-11-18 | 0.62493 | 0 | 0 | 0 | 0.52512 | 1.2323 | 0.81341
2016-11-19 | 0.72775 | 0 | 0 | 0 | 0.87759 | 1.5386 | 0.82515 | Greater than MAV
2016-11-20 | 0.72891 | 0 | 0 | 0 | 0.89507 | 1.2734 | 0.83524
2016-11-21 | 0.67807 | 0 | 0 | 0 | 0.64672 | 0.85765 | 0.81975
2016-11-22 | 0.6753 | 0 | 0 | 0 | 0.57164 | 0.70127 | 0.80343
2016-11-23 | 0.72044 | 0 | 0 | 0 | 0.82601 | 0.93422 | 0.81852
2016-11-24 | 0.57759 | 0 | 0 | 0 | 0.059084 | 0.075998 | 0.81228
2016-11-25 | 0.51234 | 0 | 0 | 0 | 0.06452 | 0.10847 | 0.80638
2016-11-26 | 0.49774 | 0 | 0 | 0 | 0.059706 | 0.11686 | 0.79286
2016-11-27 | 0.48548 | 0 | 0 | 0 | 0.059829 | 0.12931 | 0.81828
2016-11-28 | 0.49574 | 0 | 0 | 0 | 0.059858 | 0.12967 | 0.81698
2016-11-29 | 0.49559 | 0 | 0 | 0 | 0.06204 | 0.13657 | 0.76668
2016-11-30 | 0.47725 | 0 | 0 | 0 | 0.47723 | 0.54578 | 0.80165
2016-12-01 | 0.64865 | 0 | 0 | 0 | 0.91589 | 0 | 0.77231
2016-12-02 | 0.67082 | 0 | 0 | 0 | 0.92277 | 0 | 0.79595
2016-12-03 | 0.67406 | 0 | 0 | 0 | 0.92432 | 0 | 0.79186
2016-12-04 | 0.68198 | 0 | 0 | 0 | 0.93065 | 0 | 0.79186
2016-12-05 | 0.65197 | 0 | 0 | 0 | 0.50842 | 0 | 0.76729
2016-12-06 | 0.60962 | 0 | 0 | 0 | 0.18152 | 0 | 0.75749
2016-12-07 | 0.63841 | 0 | 0 | 0 | 0.2926 | 0 | 0.80399
2016-12-08 | 0.66118 | 0 | 0 | 0 | 0.26759 | 0 | 0.77937
2016-12-09 | 0.66989 | 0 | 0 | 0 | 0.28473 | 0 | 0.79831
2016-12-10 | 0.66151 | 0 | 0 | 0 | 0.28463 | 0 | 0.78902
2016-12-11 | 0.65633 | 0 | 0 | 0 | 0.25118 | 0 | 0.77404
2016-12-12 | 0.65473 | 0 | 0 | 0 | 0.25727 | 0 | 0.76454
2016-12-13 | 0.65242 | 0 | 0 | 0 | 0.26674 | 0 | 0.81373
2016-12-14 | 0.60161 | 0 | 0 | 0 | 0.18638 | 0 | 0.79834
2016-12-15 | 0.55026 | 0 | 0 | 0 | 0.61997 | 0 | 0.79068
2016-12-16 | 0.71777 | 0 | 0 | 0 | 0.93443 | 0 | 0.80441
2016-12-17 | 0.73767 | 0 | 0 | 0 | 0.9458 | 0 | 0.80879
2016-12-18 | 0.71921 | 0 | 0 | 0 | 0.94845 | 0 | 0.8002
2016-12-19 | 0.73952 | 0 | 0 | 0 | 0.95068 | 0 | 0.37929
2016-12-20 | 0.55513 | 0 | 0 | 0 | 0.64223 | 0 | 0.076006
2016-12-21 | 0.69937 | 0 | 0 | 0 | 0.94811 | 0 | 0.076264
2016-12-22 | 0.69628 | 0 | 0 | 0 | 0.93355 | 0 | 0.1374
2016-12-23 | 0.66114 | 0 | 0 | 0 | 0.59993 | 0 | 0.061278
2016-12-24 | 0.71859 | 0 | 0 | 0 | 0.9133 | 0 | 0.07306
2016-12-25 | 0.75126 | 0 | 0 | 0 | 0.89139 | 0 | 0.07436
2016-12-26 | 0.62204 | 0 | 0 | 0 | 0.235 | 0 | 0.076021
2016-12-27 | 0.68934 | 0 | 0 | 0 | 0.32296 | 0 | 0.078837
2016-12-28 | 0.63008 | 0 | 0 | 0 | 0.61929 | 0 | 0.074268
2016-12-29 | 0.6678 | 0 | 0 | 0 | 0.61134 | 0 | 0.077113
2016-12-30 | 0.81433 | 0 | 0 | 0 | 0.93784 | 0 | 0.077967
2016-12-31 | 0.74675 | 0 | 0 | 0 | 0.93081 | 0 | 0.076276
2017-01-01 | 0.69156 | 0 | 0 | 0 | 0.83686 | 0 | 0.080995
2017-01-02 | 0.6252 | 0 | 0 | 0 | 0.78215 | 0 | 0.084826
2017-01-03 | 0.64787 | 0 | 0 | 0 | 0.60744 | 0 | 0.094863
2017-01-04 | 0.65913 | 0 | 0 | 0 | 0.60807 | 0 | 0.52063
2017-01-05 | 0.65821 | 0 | 0 | 0 | 0.73429 | 0 | 0.80246
2017-01-06 | 0.57559 | 0 | 0 | 0 | 0.64403 | 0 | 0.79724
2017-01-07 | 0.76657 | 0 | 0 | 0 | 0.92905 | 0 | 0.40737
2017-01-08 | 0.64243 | 0 | 0 | 0 | 0.30447 | 0 | 0.084155
2017-01-09 | 0.47731 | 0 | 0 | 0 | 0.070616 | 0 | 0.51191
2017-01-10 | 0.48185 | 0 | 0 | 0 | 0.068377 | 0 | 0.79406
2017-01-11 | 0.49704 | 0 | 0 | 0 | 0.45885 | 0 | 0.80199
2017-01-12 | 0.79084 | 0 | 0 | 0 | 0.91083 | 0 | 0.75617
2017-01-13 | 0.74376 | 0 | 0 | 0 | 0.9149 | 0 | 0.78434
2017-01-14 | 0.78345 | 0 | 0 | 0 | 0.92741 | 0 | 0.80159
2017-01-15 | 0.80013 | 0 | 0 | 0 | 0.92464 | 0 | 0.81254
2017-01-16 | 0.78673 | 0 | 0 | 0 | 0.92412 | 0 | 0.79242
2017-01-17 | 0.66092 | 0 | 0 | 0 | 0.18687 | 0 | 0.80234
2017-01-18 | 0.54842 | 0 | 0 | 0 | 0.59761 | 1.0806 | 0.82415
2017-01-19 | 0.73095 | 0 | 0 | 0 | 0.72608 | 0.71222 | 0.83147
2017-01-20 | 0.6499 | 0 | 0 | 0 | 0.44673 | 0.40821 | 0.81166
2017-01-21 | 0.51899 | 0 | 0 | 0 | 0.3037 | 0.22984 | 0.8096
2017-01-22 | 0.49703 | 0 | 0 | 0 | 0.22369 | 0.16181 | 0.80296
2017-01-23 | 0.083722 | 0 | 0 | 0 | 0.083634 | 0.053361 | 0.79432
2017-01-24 | 0.29602 | 0 | 0 | 0 | 0.41057 | 0.30538 | 0.80532
2017-01-25 | 0.66243 | 0 | 0 | 0 | 0.51442 | 0.36935 | 0.82711
2017-01-26 | 0.85648 | 0 | 0 | 0 | 0.83637 | 0.61773 | 0.82897
2017-01-27 | 0.7864 | 0 | 0 | 0 | 0.83946 | 0.68019 | 0.81874
2017-01-28 | 0.80068 | 0 | 0 | 0 | 0.84331 | 0.78664 | 0.84311
2017-01-29 | 0.81006 | 0 | 0 | 0 | 0.84523 | 0.78237 | 0.83627
2017-01-30 | 0.80858 | 0 | 0 | 0 | 0.8534 | 0.78623 | 0.71694
2017-01-31 | 0.80961 | 0 | 0 | 0 | 0.85961 | 0.79853 | 0.84539
2017-02-01 | 0.84054 | 0 | 0 | 0 | 0.86555 | 0.80109 | 0.8284
2017-02-02 | 0.81595 | 0 | 0 | 0 | 0.59366 | 0.56483 | 0.85774
2017-02-03 | 0.70957 | 0 | 0 | 0 | 0.3644 | 0.35225 | 0.82966
2017-02-04 | 0.77155 | 0 | 0 | 0 | 0.8317 | 0.89174 | 0.82975
2017-02-05 | 0.79739 | 0 | 0 | 0 | 0.84043 | 0.91064 | 0.84179
2017-02-06 | 0.83374 | 0 | 0 | 0 | 0.86541 | 0.94251 | 0.48797
2017-02-07 | 0.81632 | 0 | 0 | 0 | 0.85857 | 0.94371 | 0.54188
2017-02-08 | 0.81127 | 0 | 0 | 0 | 0.69933 | 0.76194 | 0.81883
2017-02-09 | 0.83569 | 0 | 0 | 0 | 0.85291 | 0.94548 | 0.81715
2017-02-10 | 0.81643 | 0 | 0 | 0 | 0.84004 | 0.93532 | 0.82871
2017-02-11 | 0.81673 | 0 | 0 | 0 | 0.8408 | 0.92719 | 0.82517
2017-02-12 | 0.64294 | 0 | 0 | 0 | 0.13231 | 0.13895 | 0.82651
2017-02-13 | 0.50874 | 0 | 0 | 0 | 0.25569 | 0.27849 | 0.82056
2017-02-14 | 0.8183 | 0 | 0 | 0 | 0.84336 | 0.95301 | 0.81632
2017-02-15 | 0.6536 | 0 | 0 | 0 | 0.50731 | 0.5631 | 0.82107
2017-02-16 | 0.82388 | 0 | 0 | 0 | 0.85167 | 0.97114 | 0.80861
2017-02-17 | 0.83417 | 0 | 0 | 0 | 0.72092 | 0.81414 | 0.797
2017-02-18 | 0.75405 | 0 | 0 | 0 | 0.54232 | 0.61308 | 0.81319
2017-02-19 | 0.84843 | 0 | 0 | 0 | 0.84719 | 0.96047 | 0.81058
2017-02-20 | 0.8424 | 0 | 0 | 0 | 0.85592 | 0.96415 | 0.80492
2017-02-21 | 0.83326 | 0 | 0 | 0 | 0.86166 | 0.96259 | 0.80677
2017-02-22 | 0.78344 | 0 | 0 | 0 | 0.87016 | 0.96705 | 0.80827
2017-02-23 | 0.79015 | 0 | 0 | 0 | 0.88663 | 0.97983 | 0.81509
2017-02-24 | 0.82442 | 0 | 0 | 0 | 0.87908 | 0.96216 | 0.8289
2017-02-25 | 0.86601 | 0 | 0 | 0 | 0.89369 | 0.96617 | 0.83335
2017-02-26 | 0.891 | 0 | 0 | 0 | 0.89558 | 0.95035 | 0.82759
2017-02-27 | 0.82868 | 0 | 0 | 0 | 0.89265 | 0.93431 | 0.8282
2017-02-28 | 0.78982 | 0 | 0 | 0 | 0.88949 | 0.91763 | 0.81956
2017-03-01 | 0.79068 | 0 | 0 | 0 | 0.88901 | 0.89998 | 0.82854
2017-03-02 | 0.81278 | 0 | 0 | 0 | 0.88591 | 0.87995 | 0.82829
2017-03-03 | 0.83611 | 0 | 0 | 0 | 0.86296 | 0.835 | 0.82932
2017-03-04 | 0.85653 | 0 | 0 | 0 | 0.80598 | 0.76783 | 0.83211
2017-03-05 | 0.8193 | 0 | 0 | 0 | 0.8397 | 0.79739 | 0.83105
2017-03-06 | 0.80533 | 0 | 0 | 0 | 0.77322 | 0.36187 | 0.83306
2017-03-07 | 0.85923 | 0 | 0 | 0 | 0.87091 | 0 | 0.82663
2017-03-08 | 0.86486 | 0 | 0 | 0 | 0.87594 | 0 | 0.82992
2017-03-09 | 0.83735 | 0 | 0 | 0 | 0.8473 | 0 | 0.83464
2017-03-10 | 0.79721 | 0 | 0 | 0 | 0.83393 | 0 | 0.81884
2017-03-11 | 0.84204 | 0 | 0 | 0 | 0.83977 | 0 | 0.81862
2017-03-12 | 0.79859 | 0 | 0 | 0 | 0.31754 | 0 | 0.82336
2017-03-13 | 0.7164 | 0 | 0 | 0 | 0.16464 | 0 | 0.81414
2017-03-14 | 0.70822 | 0 | 0 | 0 | 0.39449 | 0 | 0.81454
2017-03-15 | 0.78 | 0 | 0 | 0 | 0.80946 | 0 | 0.82283
2017-03-16 | 0.76226 | 0 | 0 | 0 | 0.75073 | 0 | 0.82295
2017-03-17 | 0.77107 | 0 | 0 | 0 | 0.82671 | 0 | 0.80338
2017-03-18 | 0.84545 | 0 | 0 | 0 | 0.83258 | 0 | 0.73943
2017-03-19 | 0.72958 | 0 | 0 | 0 | 0.83798 | 0 | 0.82915
2017-03-20 | 0.4739 | 0 | 0 | 0 | 0.8359 | 0 | 0.74102
2017-03-21 | 0.46654 | 0 | 0 | 0 | 0.83572 | 0 | 0.81985
2017-03-22 | 0.6948 | 0 | 0 | 0 | 0.78602 | 0 | 0.82004
2017-03-23 | 0.86728 | 0 | 0 | 0 | 0.77884 | 0 | 0.81944
2017-03-24 | 0.85528 | 0 | 0 | 0 | 0.77437 | 0 | 0.82164
2017-03-25 | 0.89885 | 0 | 0 | 0 | 0.77557 | 0 | 0.83827
2017-03-26 | 0.9006 | 0 | 0 | 0 | 0.77294 | 0 | 0.85175
2017-03-27 | 0.88891 | 0 | 0 | 0 | 0.7781 | 0.39627 | 0.84773
2017-03-28 | 0.79835 | 0 | 0 | 0 | 0.51466 | 0.47599 | 0.85431
2017-03-29 | 0.861 | 0 | 0 | 0 | 0.85202 | 0.82309 | 0.82322
2017-03-30 | 0.81716 | 0 | 0 | 0 | 0.53868 | 0.52633 | 0.82645
2017-03-31 | 0.83627 | 0 | 0 | 0 | 0.7906 | 0.76197 | 0.82076
2017-04-01 | 0.85097 | 0 | 0 | 0 | 0.78984 | 0.75214 | 0.82371
2017-04-02 | 0.92797 | 0 | 0 | 0 | 0.84554 | 0.80715 | 0.88952
2017-04-02 23:00 | 0.83981 | 0 | 0 | 0 | 0.78196 | 0.75867 | 0.82343
2017-04-03 23:00 | 0.77792 | 0 | 0 | 0 | 0.36869 | 0.36367 | 0.83713
2017-04-04 23:00 | 0.74018 | 0 | 0 | 0 | 0.1474 | 0.15219 | 0.80109
2017-04-05 23:00 | 0.74177 | 0 | 0 | 0 | 0.23304 | 0.24245 | 0.81819
2017-04-06 23:00 | 0.73539 | 0 | 0 | 0 | 0.36718 | 0.38259 | 0.79881
2017-04-07 23:00 | 0.73064 | 0 | 0 | 0 | 0.48096 | 0.49711 | 0.80355
2017-04-08 23:00 | 0.7554 | 0 | 0 | 0 | 0.52425 | 0.53925 | 0.82406
2017-04-09 23:00 | 0.75234 | 0 | 0 | 0 | 0.43749 | 0.44913 | 0.8273
2017-04-10 23:00 | 0.66983 | 0 | 0 | 0 | 0.47425 | 0.5033 | 0.83177
2017-04-11 23:00 | 0.71191 | 0 | 0 | 0 | 0.71072 | 0.73172 | 0.82702
2017-04-12 23:00 | 0.83753 | 0 | 0 | 0 | 0.776 | 0.78569 | 0.82876
2017-04-13 23:00 | 0.80517 | 0 | 0 | 0 | 0.14942 | 0.15234 | 0.82068
2017-04-14 23:00 | 0.77049 | 0 | 0 | 0 | 0.18255 | 0.19046 | 0.81063
2017-04-15 23:00 | 0.77559 | 0 | 0 | 0 | 0.21958 | 0.22927 | 0.82157
2017-04-16 23:00 | 0.81869 | 0 | 0 | 0 | 0.25012 | 0.26029 | 0.8163
2017-04-17 23:00 | 0.53463 | 0 | 0 | 0 | 0.20384 | 0.21294 | 0.80995
2017-04-18 23:00 | 0.08978 | 0 | 0 | 0 | 0.30099 | 0.32319 | 0.83336
2017-04-19 23:00 | 0.38869 | 0 | 0 | 0 | 0.75789 | 0.78988 | 0.82729
2017-04-20 23:00 | 0.40035 | 0 | 0 | 0 | 0.76116 | 0.78003 | 0.81776
2017-04-21 23:00 | 0.45253 | 0 | 0 | 0 | 0.75356 | 0.76772 | 0.82033
2017-04-22 23:00 | 0.44829 | 0 | 0 | 0 | 0.75826 | 0.76631 | 0.82243
2017-04-23 23:00 | 0.43923 | 0 | 0 | 0 | 0.77039 | 0.77451 | 0.8088
2017-04-24 23:00 | 0.45016 | 0 | 0 | 0 | 0.76991 | 0.7716 | 0.8151
2017-04-25 23:00 | 0.40167 | 0 | 0 | 0 | 0.77208 | 0.77196 | 0.80623
2017-04-26 23:00 | 0.37799 | 0 | 0 | 0 | 0.75986 | 0.75974 | 0.8034
2017-04-27 23:00 | 0.51959 | 0 | 0 | 0 | 0.75786 | 0.7542 | 0.80809
2017-04-28 23:00 | 0.86094 | 0 | 0 | 0 | 0.69282 | 0.68814 | 0.82324
2017-04-29 23:00 | 0.83939 | 0 | 0 | 0 | 0.69035 | 0.68687 | 0.81291
2017-04-30 23:00 | 0.72613 | 0 | 0 | 0 | 0.32742 | 0.33675 | 0.80722
2017-05-01 23:00 | 0.79775 | 0 | 0 | 0 | 0.73285 | 0.74111 | 0.81429
2017-05-02 23:00 | 0.89442 | 0 | 0 | 0 | 0.73915 | 0.74146 | 0.81201
2017-05-03 23:00 | 0.8103 | 0 | 0 | 0 | 0.65974 | 0.66236 | 0.82209
2017-05-04 23:00 | 0.82049 | 0 | 0 | 0 | 0.74317 | 0.75015 | 0.82346
2017-05-05 23:00 | 0.88591 | 0 | 0 | 0 | 0.74835 | 0.75622 | 0.81113
2017-05-06 23:00 | 0.83145 | 0 | 0 | 0 | 0.74705 | 0.75413 | 0.80068
2017-05-07 23:00 | 0.80503 | 0 | 0 | 0 | 0.71058 | 0.71325 | 0.78301
2017-05-08 23:00 | 0.88425 | 0 | 0 | 0 | 0.75278 | 0.75427 | 0.80643
2017-05-09 23:00 | 0.86692 | 0 | 0 | 0 | 0.7492 | 0.74874 | 0.40934
2017-05-10 23:00 | 0.85273 | 0 | 0 | 0 | 0.75249 | 0.75383 | 0.084368
2017-05-11 23:00 | 0.80972 | 0 | 0 | 0 | 0.74599 | 0.74886 | 0.4766
2017-05-12 23:00 | 0.80838 | 0 | 0 | 0 | 0.7331 | 0.74018 | 0.83283
2017-05-13 23:00 | 0.84527 | 0 | 0 | 0 | 0.73139 | 0.74147 | 0.81478
2017-05-14 23:00 | 0.83222 | 0 | 0 | 0 | 0.73893 | 0.75218 | 0.81573
2017-05-15 23:00 | 0.81961 | 0 | 0 | 0 | 0.74089 | 0.75933 | 0.81931
2017-05-16 23:00 | 0.85285 | 0 | 0 | 0 | 0.74477 | 0.75964 | 0.82364
2017-05-17 23:00 | 0.82585 | 0 | 0 | 0 | 0.25834 | 0.26069 | 0.83006
2017-05-18 23:00 | 0.42748 | 0 | 0 | 0 | 0.040353 | 0.041564 | 0.82859
2017-05-19 23:00 | 0.27732 | 0 | 0 | 0 | 0.040311 | 0.045484 | 0.8149
2017-05-20 23:00 | 0.24441 | 0 | 0 | 0 | 0.040327 | 0.049625 | 0.80804
2017-05-21 23:00 | 0.32704 | 0 | 0 | 0 | 0.041284 | 0.050061 | 0.82503
2017-05-22 23:00 | 0.27495 | 0 | 0 | 0 | 0.044145 | 0.052289 | 0.81851
2017-05-23 23:00 | 0.19528 | 0 | 0 | 0 | 0.044146 | 0.053172 | 0.81913
2017-05-24 23:00 | 0.16999 | 0 | 0 | 0 | 0.040741 | 0.050224 | 0.82105
2017-05-25 23:00 | 0.2267 | 0 | 0 | 0 | 0.18133 | 0.2267 | 0.82248
2017-05-26 23:00 | 0.39045 | 0 | 0 | 0 | 0.44275 | 0.55043 | 0.82292
2017-05-27 23:00 | 0.75463 | 0 | 0 | 0 | 0.75019 | 0.91978 | 0.82043
2017-05-28 23:00 | 0.6571 | 0 | 0 | 0 | 0.40095 | 0.48332 | 0.83689
2017-05-29 23:00 | 0.33543 | 0 | 0 | 0 | 0.048511 | 0.058285 | 0.82531
2017-05-30 23:00 | 0.24031 | 0 | 0 | 0 | 0.040556 | 0.049735 | 0.80948
2017-05-31 23:00 | 0.12551 | 0 | 0 | 0 | 0.041684 | 0.051777 | 0.82332
2017-06-01 23:00 | 0.083682 | 0 | 0 | 0 | 0.040642 | 0.050495 | 0.84218
2017-06-02 23:00 | 0.09495 | 0 | 0 | 0 | 0.040307 | 0.050075 | 0.83915
2017-06-03 23:00 | 0.073709 | 0 | 0 | 0 | 0.040293 | 0.050068 | 0.81964
2017-06-04 23:00 | 0.095213 | 0 | 0 | 0 | 0.036004 | 0.04604 | 0.81535
2017-06-05 23:00 | 0.093475 | 0 | 0 | 0 | 0.031605 | 0.041929 | 0.8231
2017-06-06 23:00 | 0.073267 | 0 | 0 | 0 | 0.03508 | 0.04644 | 0.82474
2017-06-07 23:00 | 0.065209 | 0 | 0 | 0 | 0.034182 | 0.045031 | 0.85216
2017-06-08 23:00 | 0.069663 | 0 | 0 | 0 | 0.03961 | 0.050061 | 0.84654
2017-06-09 23:00 | 0.073243 | 0 | 0 | 0 | 0.040293 | 0.050115 | 0.85065
2017-06-10 23:00 | 0.071612 | 0 | 0 | 0 | 0.040293 | 0.051135 | 0.86264
2017-06-11 23:00 | 0.068381 | 0 | 0 | 0 | 0.040293 | 0.05361 | 0.87066
2017-06-12 23:00 | 0.07313 | 0 | 0 | 0 | 0.041639 | 0.058163 | 0.85651
2017-06-13 23:00 | 0.073499 | 0 | 0 | 0 | 0.041402 | 0.057205 | 0.85081
2017-06-14 23:00 | 0.072123 | 0 | 0 | 0 | 0.040293 | 0.054071 | 0.85913
2017-06-15 23:00 | 0.071797 | 0 | 0 | 0 | 0.040293 | 0.055989 | 0.86712
2017-06-16 23:00 | 0.073215 | 0 | 0 | 0 | 0.040293 | 0.058682 | 0.87308
2017-06-17 23:00 | 0.078905 | 0 | 0 | 0 | 0.040395 | 0.058637 | 0.87405
2017-06-18 23:00 | 0.07383 | 0 | 0 | 0 | 0.042116 | 0.059829 | 0.87095
2017-06-19 23:00 | 0.074397 | 0 | 0 | 0 | 0.042103 | 0.059829 | 0.8515
2017-06-20 23:00 | 0.075579 | 0 | 0 | 0 | 0.042784 | 0.059829 | 0.8687
2017-06-21 23:00 | 0.075196 | 0 | 0 | 0 | 0.043348 | 0.059887 | 0.85952
2017-06-22 23:00 | 0.078917 | 0 | 0 | 0 | 0.042813 | 0.059628 | 0.82609
2017-06-23 23:00 | 0.077644 | 0 | 0 | 0 | 0.03896 | 0.051028 | 0.85957
2017-06-24 23:00 | 0.07598 | 0 | 0 | 0 | 0.040293 | 0.055393 | 0.84868
2017-06-25 23:00 | 0.075987 | 0 | 0 | 0 | 0.040293 | 0.054658 | 0.87863
2017-06-26 23:00 | 0.074622 | 0 | 0 | 0 | 0.040243 | 0.054827 | 0.87149
2017-06-27 23:00 | 0.077365 | 0 | 0 | 0 | 0.041135 | 0.059796 | 0.87219
2017-06-28 23:00 | 0.075429 | 0 | 0 | 0 | 0.043107 | 0.059829 | 0.73743
2017-06-29 23:00 | 0.075599 | 0 | 0 | 0 | 0.043712 | 0.059795 | 0.83774
2017-06-30 23:00 | 0.076332 | 0 | 0 | 0 | 0.048295 | 0.059829 | 0.87164

## 17-18
Date Stamp | .Gear Island 1050 Fluoride | .Gear Island 1050 Fluoride Analyser #2 | .Te Marua PS Fluoride Residual | .Te Marua TP Fluoride Residual | .Wainui Fluoride Building Fluoride Residual Stream 1 | .Wainui Fluoride Building Fluoride Residual Stream 2 | .Waterloo Naenae Fluoride Residual
2017-07-01 23:00 | 0.07657 | 0 | 0 | 0 | 0.047156 | 0.059866 | 0.86156
2017-07-02 23:00 | 0.073075 | 0 | 0 | 0 | 0.0458 | 0.060321 | 0.86507
2017-07-03 23:00 | 0.073823 | 0 | 0 | 0 | 0.049606 | 0.059987 | 0.85195 |  | Analysers not installed or was off
2017-07-04 23:00 | 0.074721 | 0 | 0 | 0 | 0.047898 | 0.059788 | 0.86491 |  | Fluoride not dosed
2017-07-05 23:00 | 0.069427 | 0 | 0 | 0 | 0.049477 | 0.059829 | 0.4402 |  | fluoride dosed but outside recommended range
2017-07-06 23:00 | 0.072881 | 0 | 0 | 0 | 0.05 | 0.059829 | 0.50626 |  | Fluoride dosed but within recommended range
2017-07-07 23:00 | 0.068813 | 0 | 0 | 0 | 0.04965 | 0.059829 | 0.84647
2017-07-08 23:00 | 0.071379 | 0 | 0 | 0 | 0.049959 | 0.059829 | 0.85244 | Assumptions: |  | 1. Values less than 0.1 indicates that fluoride is not being dosed
2017-07-09 23:00 | 0.072944 | 0 | 0 | 0 | 0.049736 | 0.059829 | 0.863 |  |  | 2. The Gear Island sampling point is downstream of the plant and can contain a residual from the Wainuiomata WTP
2017-07-10 23:00 | 0.070805 | 0 | 0 | 0 | 0.04859 | 0.059666 | 0.85955
2017-07-11 23:00 | 0.08152 | 0 | 0 | 0 | 0.049729 | 0.061219 | 0.84954
2017-07-12 23:00 | 0.093079 | 0 | 0 | 0 | 0.07663 | 0.094922 | 0.80464
2017-07-13 23:00 | 0.095654 | 0 | 0 | 0 | 0.085081 | 0.10434 | 0.62718
2017-07-14 23:00 | 0.080301 | 0 | 0 | 0 | 0.034423 | 0.043882 | 0.44914
2017-07-15 23:00 | 0.065838 | 0 | 0 | 0 | 0.031537 | 0.041574 | 0.28617
2017-07-16 23:00 | 0.068096 | 0 | 0 | 0 | 0.037061 | 0.048378 | 0.090858
2017-07-17 23:00 | 0.20902 | 0 | 0 | 0 | 0.47868 | 0.46776 | 0.40839
2017-07-18 23:00 | 0.61914 | 0 | 0 | 0 | 0.94262 | 0.77138 | 0.84568
2017-07-19 23:00 | 0.47727 | 0 | 0 | 0 | 0.73757 | 0.58252 | 0.83746
2017-07-20 23:00 | 0.44998 | 0 | 0 | 0 | 0.91004 | 0.72498 | 0.86232
2017-07-21 23:00 | 0.41808 | 0 | 0 | 0 | 0.88871 | 0.7427 | 0.85028
2017-07-22 23:00 | 0.5178 | 0 | 0 | 0 | 0.88236 | 0.73915 | 0.85215
2017-07-23 23:00 | 0.61569 | 0 | 0 | 0 | 0.94176 | 0.80235 | 0.84789
2017-07-24 23:00 | 0.44944 | 0 | 0 | 0 | 0.68571 | 0.56656 | 0.84429
2017-07-25 23:00 | 0.4152 | 0 | 0 | 0 | 0.74281 | 0.61228 | 0.87833
2017-07-26 23:00 | 0.4545 | 0 | 0 | 0 | 0.94423 | 0.78425 | 0.84432
2017-07-27 23:00 | 0.43786 | 0 | 0 | 0 | 0.92757 | 0.77913 | 0.85462
2017-07-28 23:00 | 0.45641 | 0 | 0 | 0 | 0.9347 | 0.77637 | 0.85824
2017-07-29 23:00 | 0.45686 | 0 | 0 | 0 | 0.95959 | 0.7885 | 0.85189
2017-07-30 23:00 | 0.46542 | 0 | 0 | 0 | 0.98444 | 0.80265 | 0.22491
2017-07-31 23:00 | 0.40712 | 0 | 0 | 0 | 0.94531 | 0.7771 | 0.094179
2017-08-01 23:00 | 0.4764 | 0 | 0 | 0 | 0.93853 | 0.78879 | 0.090456
2017-08-02 23:00 | 0.37881 | 0 | 0 | 0 | 0.74246 | 0.61908 | 0.094171
2017-08-03 23:00 | 0.47425 | 0 | 0 | 0 | 0.91728 | 0.80998 | 0.099722
2017-08-04 23:00 | 0.48557 | 0 | 0 | 0 | 0.82352 | 0.80825 | 0.096585
2017-08-05 23:00 | 0.46224 | 0 | 0 | 0 | 0.83075 | 0.81642 | 0.091874
2017-08-06 23:00 | 0.49583 | 0 | 0 | 0 | 0.8418 | 0.82372 | 0.096728
2017-08-07 23:00 | 0.6568 | 0 | 0 | 0 | 0.86462 | 0.85485 | 0.094337
2017-08-08 23:00 | 0.62746 | 0 | 0 | 0 | 0.82468 | 0.81497 | 0.089865
2017-08-09 23:00 | 0.3494 | 0 | 0 | 0 | 0.78377 | 0.76641 | 0.094999
2017-08-10 23:00 | 0.42119 | 0 | 0 | 0 | 0.78899 | 0.77483 | 0.08712
2017-08-11 23:00 | 0.46428 | 0 | 0 | 0 | 0.80248 | 0.79568 | 0.088963
2017-08-12 23:00 | 0.39072 | 0 | 0 | 0 | 0.75182 | 0.74723 | 0.092482
2017-08-13 23:00 | 0.20025 | 0 | 0 | 0 | 0.059408 | 0.050837 | 0.093609
2017-08-14 23:00 | 0.11746 | 0 | 0 | 0 | 0.35129 | 0.33298 | 0.085538
2017-08-15 23:00 | 0.58691 | 0 | 0 | 0 | 0.83946 | 0.81592 | 0.08585
2017-08-16 23:00 | 0.72204 | 0 | 0 | 0 | 0.84921 | 0.83584 | 0.087133
2017-08-17 23:00 | 0.51105 | 0 | 0 | 0 | 0.47404 | 0.45952 | 0.15038
2017-08-18 23:00 | 0.13809 | 0 | 0 | 0 | 0.39368 | 0.37527 | 0.08866
2017-08-19 23:00 | 0.59636 | 0 | 0 | 0 | 0.74413 | 0.72997 | 0.088843
2017-08-20 23:00 | 0.64637 | 0 | 0 | 0 | 0.84155 | 0.8212 | 0.082191
2017-08-21 23:00 | 0.62044 | 0 | 0 | 0 | 0.85886 | 0.83285 | 0.084731
2017-08-22 23:00 | 0.56202 | 0 | 0 | 0 | 0.83294 | 0.80599 | 0.089675
2017-08-23 23:00 | 0.5025 | 0 | 0 | 0 | 0.82653 | 0.78517 | 0.090675
2017-08-24 23:00 | 0.45667 | 0 | 0 | 0 | 0.81426 | 0.77879 | 0.091872
2017-08-25 23:00 | 0.39882 | 0 | 0 | 0 | 0.80133 | 0.77776 | 0.090729
2017-08-26 23:00 | 0.38762 | 0 | 0 | 0 | 0.7969 | 0.77795 | 0.091914
2017-08-27 23:00 | 0.3822 | 0 | 0 | 0 | 0.79278 | 0.7804 | 0.090477
2017-08-28 23:00 | 0.42289 | 0 | 0 | 0 | 0.79241 | 0.77303 | 0.086457
2017-08-29 23:00 | 0.5353 | 0 | 0 | 0 | 0.80788 | 0.78735 | 0.090381
2017-08-30 23:00 | 0.39429 | 0 | 0 | 0 | 0.78928 | 0.77481 | 0.087889
2017-08-31 23:00 | 0.34854 | 0 | 0 | 0 | 0.76112 | 0.74512 | 0.09002
2017-09-01 23:00 | 0.29156 | 0 | 0 | 0 | 0.75071 | 0.73307 | 0.088828
2017-09-02 23:00 | 0.40233 | 0 | 0 | 0 | 0.75739 | 0.73805 | 0.089916
2017-09-03 23:00 | 0.40259 | 0 | 0 | 0 | 0.77268 | 0.74548 | 0.090883
2017-09-04 23:00 | 0.40257 | 0 | 0 | 0 | 0.78645 | 0.75334 | 0.087457
2017-09-05 23:00 | 0.40247 | 0 | 0 | 0 | 0.7021 | 0.66897 | 0.091246
2017-09-06 23:00 | 0.40241 | 0 | 0 | 0 | 0.099481 | 0.092969 | 0.08558
2017-09-07 23:00 | 0.40252 | 0 | 0 | 0 | 0.52936 | 0.51969 | 0.089561
2017-09-08 23:00 | 0.40254 | 0 | 0 | 0 | 0.53886 | 0.52659 | 0.090238
2017-09-09 23:00 | 0.40256 | 0 | 0 | 0 | 0.71874 | 0.69691 | 0.092019
2017-09-10 23:00 | 0.40256 | 0 | 0 | 0 | 0.81109 | 0.79745 | 0.089888
2017-09-11 23:00 | 0.40257 | 0 | 0 | 0 | 0.82095 | 0.80855 | 0.089449
2017-09-12 23:00 | 0.40251 | 0 | 0 | 0 | 0.84072 | 0.81968 | 0.089277
2017-09-13 23:00 | 0.40242 | 0 | 0 | 0 | 0.81771 | 0.81745 | 0.091478
2017-09-14 23:00 | 0.4024 | 0 | 0 | 0 | 0.7901 | 0.79551 | 0.086628
2017-09-15 23:00 | 0.40238 | 0 | 0 | 0 | 0.78451 | 0.78677 | 0.089411
2017-09-16 23:00 | 0.40241 | 0 | 0 | 0 | 0.77357 | 0.77759 | 0.089056
2017-09-17 23:00 | 0.40243 | 0 | 0 | 0 | 0.7682 | 0.77033 | 0.093118
2017-09-18 23:00 | 0.44446 | 0 | 0 | 0 | 0.74341 | 0.74432 | 0.089187
2017-09-19 23:00 | 0.42938 | 0 | 0 | 0 | 0.71608 | 0.71145 | 0.10606
2017-09-20 23:00 | 0.46967 | 0 | 0 | 0 | 0.81418 | 0.81852 | 0.088889
2017-09-21 23:00 | 0.27645 | 0 | 0 | 0 | 0.22303 | 0.2142 | 0.089566
2017-09-22 23:00 | 0.078212 | 0 | 0 | 0 | 0.049541 | 0.034177 | 0.086667
2017-09-23 23:00 | 0.076415 | 0 | 0 | 0 | 0.050353 | 0.038245 | 0.08722
2017-09-25 | 0.10736 | 0 | 0 | 0 | 0.10149 | 0.09083 | 0.087328
2017-09-26 | 0.086708 | 0 | 0 | 0 | 0.2636 | 0.26416 | 0.16807
2017-09-27 | 0.34273 | 0 | 0 | 0 | 0.72572 | 0.76142 | 0.53727
2017-09-28 | 0.46986 | 0 | 0 | 0 | 0.79687 | 0.78316 | 0.83792
2017-09-29 | 0.44705 | 0 | 0 | 0 | 0.56451 | 0.55279 | 0.83714
2017-09-30 | 0.084275 | 0 | 0 | 0 | 0.049324 | 0.053923 | 0.84142
2017-10-01 | 0.076265 | 0 | 0 | 0 | 0.047598 | 0.052802 | 0.83853
2017-10-02 | 0.074217 | 0 | 0 | 0 | 0.047391 | 0.053791 | 0.82653
2017-10-03 | 0.072922 | 0 | 0 | 0 | 0.047377 | 0.055836 | 0.84238
2017-10-04 | 0.074225 | 0 | 0 | 0 | 0.049173 | 0.05825 | 0.83862
2017-10-05 | 0.075417 | 0 | 0 | 0 | 0.04996 | 0.059816 | 0.83362
2017-10-06 | 0.075102 | 0 | 0 | 0 | 0.048999 | 0.059062 | 0.82959
2017-10-07 | 0.076726 | 0 | 0 | 0 | 0.050034 | 0.059829 | 0.84694
2017-10-08 | 0.077061 | 0 | 0 | 0 | 0.047025 | 0.054676 | 0.84632
2017-10-09 | 0.07704 | 0 | 0 | 0 | 0.04683 | 0.052511 | 0.84154
2017-10-10 | 0.074468 | 0 | 0 | 0 | 0.04108 | 0.050061 | 0.8223
2017-10-11 | 0.074552 | 0 | 0 | 0 | 0.04135 | 0.050082 | 0.32287
2017-10-12 | 0.076149 | 0 | 0 | 0 | 0.036358 | 0.042032 | 0.81993
2017-10-13 | 0.070887 | 0 | 0 | 0 | 0.040013 | 0.047564 | 0.83309
2017-10-14 | 0.071932 | 0 | 0 | 0 | 0.040763 | 0.050061 | 0.82414
2017-10-15 | 0.072032 | 0 | 0 | 0 | 0.041466 | 0.050289 | 0.84065
2017-10-16 | 0.070655 | 0 | 0 | 0 | 0.042155 | 0.051201 | 0.84201
2017-10-17 | 0.07179 | 0 | 0 | 0 | 0.044775 | 0.05409 | 0.83865
2017-10-18 | 0.072174 | 0 | 0 | 0 | 0.044757 | 0.054302 | 0.83335
2017-10-19 | 0.073469 | 0 | 0 | 0 | 0.044796 | 0.053804 | 0.75647
2017-10-20 | 0.073545 | 0 | 0 | 0 | 0.047537 | 0.057767 | 0.82817
2017-10-21 | 0.073342 | 0 | 0 | 0 | 0.049976 | 0.059829 | 0.8321
2017-10-22 | 0.074016 | 0 | 0 | 0 | 0.049795 | 0.059976 | 0.83469
2017-10-23 | 0.074062 | 0 | 0 | 0 | 0.049961 | 0.05986 | 0.83055
2017-10-24 | 0.074047 | 0 | 0 | 0 | 0.052182 | 0.063651 | 0.83443
2017-10-25 | 0.077592 | 0 | 0 | 0 | 0.052535 | 0.068321 | 0.84137
2017-10-26 | 0.076765 | 0 | 0 | 0 | 0.050362 | 0.065805 | 0.82114
2017-10-27 | 0.076773 | 0 | 0 | 0 | 0.05008 | 0.061887 | 0.83996
2017-10-28 | 0.075268 | 0 | 0 | 0 | 0.049708 | 0.061632 | 0.8313
2017-10-29 | 0.07651 | 0 | 0 | 0 | 0.050329 | 0.061588 | 0.82409
2017-10-30 | 0.077247 | 0 | 0 | 0 | 0.051421 | 0.063593 | 0.8285
2017-10-31 | 0.076335 | 0 | 0 | 0 | 0.052128 | 0.060948 | 0.57907
2017-11-01 | 0.077583 | 0 | 0 | 0 | 0.05274 | 0.062743 | 0.56739
2017-11-02 | 0.077187 | 0 | 0 | 0 | 0.051626 | 0.05976 | 0.82964
2017-11-03 | 0.07616 | 0 | 0 | 0 | 0.05055 | 0.059809 | 0.83195
2017-11-04 | 0.077405 | 0 | 0 | 0 | 0.050661 | 0.056822 | 0.83236
2017-11-05 | 0.078268 | 0 | 0 | 0 | 0.050336 | 0.051537 | 0.8354
2017-11-06 | 0.07649 | 0 | 0 | 0 | 0.050061 | 0.050054 | 0.84097
2017-11-07 | 0.076392 | 0 | 0 | 0 | 0.050041 | 0.054288 | 0.46594
2017-11-08 | 0.076602 | 0 | 0 | 0 | 0.048956 | 0.059497 | 0.085274
2017-11-09 | 0.072641 | 0 | 0 | 0 | 0.044885 | 0.056386 | 0.087727
2017-11-10 | 0.07499 | 0 | 0 | 0 | 0.056531 | 0.079845 | 0.40193
2017-11-11 | 0.074355 | 0 | 0 | 0 | 0.041783 | 0.068157 | 0.4111
2017-11-12 | 0.073433 | 0 | 0 | 0 | 0.041286 | 0.069991 | 0.087178
2017-11-13 | 0.07232 | 0 | 0 | 0 | 0.041578 | 0.066715 | 0.082634
2017-11-14 | 0.072007 | 0 | 0 | 0 | 0.040292 | 0.064256 | 0.48797
2017-11-15 | 0.071831 | 0 | 0 | 0 | 0.041078 | 0.068248 | 0.81748
2017-11-16 | 0.075271 | 0 | 0 | 0 | 0.044065 | 0.071069 | 0.81763
2017-11-17 | 0.20409 | 0 | 0 | 0 | 0.39345 | 0.52702 | 0.81976
2017-11-18 | 0.569 | 0 | 0 | 0 | 0.81827 | 1.0712 | 0.83152
2017-11-19 | 0.56431 | 0 | 0 | 0 | 0.81035 | 1.0743 | 0.83618
2017-11-20 | 0.53439 | 0 | 0 | 0 | 0.75598 | 0.88151 | 0.83417
2017-11-21 | 0.45014 | 0 | 0 | 0 | 0.66305 | 0.66732 | 0.82799
2017-11-22 | 0.39761 | 0 | 0 | 0 | 0.64075 | 0.66097 | 0.82522
2017-11-23 | 0.37329 | 0 | 0 | 0 | 0.71869 | 0.73263 | 0.81481
2017-11-24 | 0.37836 | 0 | 0 | 0 | 0.79247 | 0.75672 | 0.81292
2017-11-25 | 0.29302 | 0 | 0 | 0 | 0.82132 | 0.79038 | 0.81762
2017-11-26 | 0.1806 | 0 | 0 | 0 | 0.45648 | 0.44439 | 0.81554
2017-11-27 | 0.13272 | 0 | 0 | 0 | 0.41911 | 0.38593 | 0.81406
2017-11-28 | 0.12938 | 0 | 0 | 0 | 0.16107 | 0.13792 | 0.81344
2017-11-29 | 0.085508 | 0 | 0 | 0 | 0.087111 | 0.060608 | 0.74961
2017-11-30 | 0.13801 | 0 | 0 | 0 | 0.55445 | 0.50187 | 0.80647
2017-12-01 | 0.23514 | 0 | 0 | 0 | 0.77132 | 0.70521 | 0.78766
2017-12-02 | 0.2802 | 0 | 0 | 0 | 0.85843 | 0.77954 | 0.80489
2017-12-03 | 0.26866 | 0 | 0 | 0 | 0.83763 | 0.78941 | 0.8087
2017-12-04 | 0.25272 | 0 | 0 | 0 | 0.59761 | 0.55417 | 0.80503
2017-12-05 | 0.1555 | 0 | 0 | 0 | 0.60291 | 0.55407 | 0.76431
2017-12-06 | 0.24522 | 0 | 0 | 0 | 0.85891 | 0.79783 | 0.44913
2017-12-07 | 0.2481 | 0 | 0 | 0 | 0.8458 | 0.79541 | 0.48494
2017-12-08 | 0.25206 | 0 | 0 | 0 | 0.85296 | 0.79888 | 0.75069
2017-12-09 | 0.22782 | 0 | 0 | 0 | 0.83908 | 0.80189 | 0.80835
2017-12-10 | 0.25165 | 0 | 0 | 0 | 0.81475 | 0.78504 | 0.80292
2017-12-11 | 0.24608 | 0 | 0 | 0 | 0.85474 | 0.7747 | 0.80578
2017-12-12 | 0.21543 | 0 | 0 | 0 | 0.8371 | 0.73867 | 0.79747
2017-12-13 | 0.15724 | 0 | 0 | 0 | 0.54513 | 0.461 | 0.77308
2017-12-14 | 0.25385 | 0 | 0 | 0 | 0.90407 | 0.79722 | 0.8054
2017-12-15 | 0.28336 | 0 | 0 | 0 | 0.82082 | 0.76715 | 0.80876
2017-12-16 | 0.20686 | 0 | 0 | 0 | 0.83975 | 0.80136 | 0.80313
2017-12-17 | 0.20211 | 0 | 0 | 0 | 0.49224 | 0.47654 | 0.79894
2017-12-18 | 0.13492 | 0 | 0 | 0 | 0.57177 | 0.54591 | 0.80758
2017-12-19 | 0.1839 | 0 | 0 | 0 | 0.27834 | 0.26321 | 0.81216
2017-12-20 | 0.090421 | 0 | 0 | 0 | 0.069377 | 0.064212 | 0.81955
2017-12-21 | 0.084256 | 0 | 0 | 0 | 0.063829 | 0.070138 | 0.81204
2017-12-22 | 0.077742 | 0 | 0 | 0 | 0.066644 | 0.070243 | 0.81662
2017-12-23 | 0.077483 | 0 | 0 | 0 | 0.067903 | 0.070884 | 0.80983
2017-12-24 | 0.080112 | 0 | 0 | 0 | 0.067166 | 0.073599 | 0.81021
2017-12-25 | 0.080939 | 0 | 0 | 0 | 0.070165 | 0.075592 | 0.8109
2017-12-26 | 0.082316 | 0 | 0 | 0 | 0.066059 | 0.070216 | 0.81488
2017-12-27 | 0.14015 | 0 | 0 | 0 | 0.49153 | 0.49962 | 0.80526
2017-12-28 | 0.28757 | 0 | 0 | 0 | 0.79405 | 0.79028 | 0.80387
2017-12-29 | 0.28921 | 0 | 0 | 0 | 0.79136 | 0.78897 | 0.80526
2017-12-30 | 0.26553 | 0 | 0 | 0 | 0.78891 | 0.7967 | 0.80467
2017-12-31 | 0.24513 | 0 | 0 | 0 | 0.80195 | 0.80227 | 0.80907
2018-01-01 | 0.25988 | 0 | 0 | 0 | 0.81626 | 0.81556 | 0.79626
2018-01-02 | 0.19661 | 0 | 0 | 0 | 0.82905 | 0.82717 | 0.80218
2018-01-03 | 0.20318 | 0 | 0 | 0 | 0.83447 | 0.82315 | 0.80132
2018-01-04 | 0.22009 | 0 | 0 | 0 | 0.73729 | 0.7144 | 0.80932
2018-01-05 | 0.18429 | 0 | 0 | 0 | 0.74371 | 0.71208 | 0.81239
2018-01-06 | 0.084255 | 0 | 0 | 0 | 0.10626 | 0.097213 | 0.80445
2018-01-07 | 0.080651 | 0 | 0 | 0 | 0.16446 | 0.15422 | 0.81173
2018-01-08 | 0.081378 | 0 | 0 | 0 | 0.13087 | 0.1224 | 0.80595
2018-01-09 | 0.31559 | 0 | 0 | 0 | 0.56699 | 0.54089 | 0.81489
2018-01-10 | 0.69139 | 0 | 0 | 0 | 0.84108 | 0.79678 | 0.66377
2018-01-11 | 0.71673 | 0 | 0 | 0 | 0.86038 | 0.80343 | 0.80955
2018-01-12 | 0.63197 | 0 | 0 | 0 | 0.85459 | 0.80871 | 0.65462
2018-01-13 | 0.25183 | 0 | 0 | 0 | 0.8441 | 0.80262 | 0.83979
2018-01-14 | 0.39081 | 0 | 0 | 0 | 0.83102 | 0.79156 | 0.73765
2018-01-15 | 0.47252 | 0 | 0 | 0 | 0.81621 | 0.76839 | 0.6323
2018-01-16 | 0.38863 | 0 | 0 | 0 | 0.86233 | 0.8011 | 0.84498
2018-01-17 | 0.30645 | 0 | 0 | 0 | 0.87385 | 0.80769 | 0.79134
2018-01-18 | 0.30667 | 0 | 0 | 0 | 0.87615 | 0.79399 | 0.80195
2018-01-19 | 0.29357 | 0 | 0 | 0 | 0.86224 | 0.78777 | 0.81444
2018-01-20 | 0.30141 | 0 | 0 | 0 | 0.85868 | 0.79441 | 0.79565
2018-01-21 | 0.37779 | 0 | 0 | 0 | 0.8602 | 0.79444 | 0.80125
2018-01-22 | 0.24475 | 0 | 0 | 0 | 0.86553 | 0.79085 | 0.82101
2018-01-23 | 0.24966 | 0 | 0 | 0 | 0.88203 | 0.80796 | 0.82101
2018-01-24 | 0.21777 | 0 | 0 | 0 | 0.54521 | 0.49521 | 0.82101
2018-01-25 | 0.11868 | 0 | 0 | 0 | 0.55763 | 0.50964 | 0.82101
2018-01-26 | 0.25701 | 0 | 0 | 0 | 0.90691 | 0.81709 | 0.82101
2018-01-27 | 0.23407 | 0 | 0 | 0 | 0.90723 | 0.81653 | 0.82101
2018-01-28 | 0.21772 | 0 | 0 | 0 | 0.90919 | 0.82338 | 0.82101
2018-01-29 | 0.19456 | 0 | 0 | 0 | 0.64925 | 0.58266 | 0.82101
2018-01-30 | 0.20027 | 0 | 0 | 0 | 0.53964 | 0.49084 | 0.82101
2018-01-31 | 0.40546 | 0 | 0 | 0 | 0.62636 | 0.55874 | 0.82101
2018-02-01 | 0.58401 | 0 | 0 | 0 | 0.87131 | 0.77836 | 0.27911
2018-02-02 | 0.27986 | 0 | 0 | 0 | 0.74607 | 0.66376 | 0
2018-02-03 | 0.25924 | 0 | 0 | 0 | 0.66584 | 0.58723 | 0
2018-02-04 | 0.12258 | 0 | 0 | 0 | 0.071246 | 0.061221 | 0
2018-02-05 | 0.082921 | 0 | 0 | 0 | 0.34243 | 0.31631 | 0
2018-02-06 | 0.15086 | 0 | 0 | 0 | 0.81453 | 0.75374 | 0
2018-02-07 | 0.15975 | 0 | 0 | 0 | 0.82004 | 0.81589 | 0
2018-02-08 | 0.16357 | 0 | 0 | 0 | 0.83238 | 0.8699 | 0
2018-02-09 | 0.1557 | 0 | 0 | 0 | 0.68863 | 0.71687 | 0
2018-02-10 | 0.13442 | 0 | 0 | 0 | 0.074776 | 0.073823 | 0
2018-02-11 | 0.091349 | 0 | 0 | 0 | 0.091251 | 0.09249 | 0
2018-02-12 | 0.091208 | 0 | 0 | 0 | 0.12339 | 0.12694 | 0
2018-02-13 | 0.13024 | 0 | 0 | 0 | 0.28592 | 0.30273 | 0
2018-02-14 | 0.11486 | 0 | 0 | 0 | 0.51467 | 0.52539 | 0
2018-02-15 | 0.21556 | 0 | 0 | 0 | 0.77382 | 0.784 | 0
2018-02-16 | 0.21713 | 0 | 0 | 0 | 0.77045 | 0.78286 | 0
2018-02-17 | 0.16832 | 0 | 0 | 0 | 0.64351 | 0.65582 | 0
2018-02-18 | 0.20145 | 0 | 0 | 0 | 0.78 | 0.80271 | 0
2018-02-19 | 0.20426 | 0 | 0 | 0 | 0.78256 | 0.80125 | 0
2018-02-20 | 0.15628 | 0 | 0 | 0 | 0.47177 | 0.47246 | 0
2018-02-21 | 0.087387 | 0 | 0 | 0 | 0.18652 | 0.1839 | 0
2018-02-22 | 0.11071 | 0 | 0 | 0 | 0.4417 | 0.44121 | 0.66708
2018-02-23 | 0.27326 | 0 | 0 | 0 | 0.75991 | 0.77403 | 2 | MAV Exceeded
2018-02-24 | 0.19809 | 0 | 0 | 0 | 0.58587 | 0.59156 | 2 | MAV Exceeded
2018-02-25 | 0.089174 | 0 | 0 | 0 | 0.16901 | 0.16814 | 2 | MAV Exceeded
2018-02-26 | 0.11608 | 0 | 0 | 0 | 0.42776 | 0.42918 | 2 | MAV Exceeded
2018-02-27 | 0.2645 | 0 | 0 | 0 | 0.7459 | 0.78179 | 2 | MAV Exceeded
2018-02-28 | 0.27284 | 0 | 0 | 0 | 0.75895 | 0.78843 | 2 | MAV Exceeded
2018-03-01 | 0.27813 | 0 | 0 | 0 | 0.75348 | 0.79339 | 2 | MAV Exceeded
2018-03-02 | 0.23769 | 0 | 0 | 0 | 0.7203 | 0.75244 | 1.3167
2018-03-03 | 0.18614 | 0 | 0 | 0 | 0.76027 | 0.80101 | 0.81818
2018-03-04 | 0.18942 | 0 | 0 | 0 | 0.7649 | 0.80972 | 0.79954
2018-03-05 | 0.2616 | 0 | 0 | 0 | 0.76847 | 0.8116 | 0.75742
2018-03-06 | 0.29586 | 0 | 0 | 0 | 0.75953 | 0.80554 | 0.10948
2018-03-07 | 0.26827 | 0 | 0 | 0 | 0.76776 | 0.80519 | 0.18087
2018-03-08 | 0.32566 | 0 | 0 | 0 | 0.73496 | 0.7954 | 0.12056
2018-03-09 | 0.27536 | 0 | 0 | 0 | 0.75228 | 0.81193 | 0.10577
2018-03-10 | 0.2567 | 0 | 0 | 0 | 0.76428 | 0.81684 | 0.081641
2018-03-11 | 0.25017 | 0 | 0 | 0 | 0.7629 | 0.82018 | 0.081374
2018-03-12 | 0.26749 | 0 | 0 | 0 | 0.7597 | 0.81807 | 0.080904
2018-03-13 | 0.2812 | 0 | 0 | 0 | 0.76457 | 0.819 | 0.10349
2018-03-14 | 0.26709 | 0 | 0 | 0 | 0.73613 | 0.80401 | 0.49083
2018-03-15 | 0.3326 | 0 | 0 | 0 | 0.634 | 0.69948 | 0.75502
2018-03-16 | 0.25078 | 0 | 0 | 0 | 0.62394 | 0.69996 | 0.79905
2018-03-17 | 0.22161 | 0 | 0 | 0 | 0.61692 | 0.70856 | 0.79135
2018-03-18 | 0.20943 | 0 | 0 | 0 | 0.55398 | 0.64392 | 0.13189
2018-03-19 | 0.21575 | 0 | 0 | 0 | 0.41112 | 0.4774 | 0.45692
2018-03-20 | 0.10879 | 0 | 0 | 0 | 0.076272 | 0.08822 | 0.38604
2018-03-21 | 0.1217 | 0 | 0 | 0 | 0.39238 | 0.47292 | 0.084279
2018-03-22 | 0.19954 | 0 | 0 | 0 | 0.53532 | 0.55938 | 0.57906
2018-03-23 | 0.12321 | 0 | 0 | 0 | 0.28976 | 0.27887 | 0.76803
2018-03-24 | 0.11009 | 0 | 0 | 0 | 0.11197 | 0.07775 | 0.12246
2018-03-25 | 0.081457 | 0 | 0 | 0 | 0.11384 | 0.070135 | 0.082209
2018-03-26 | 0.089682 | 0 | 0 | 0 | 0.16814 | 0.099174 | 0.08211
2018-03-27 | 0.10172 | 0 | 0 | 0 | 0.28655 | 0.14608 | 0.49581
2018-03-28 | 0.10671 | 0 | 0 | 0 | 0.23834 | 0.12535 | 0.79716
2018-03-29 | 0.092652 | 0 | 0 | 0 | 0.11561 | 0.077016 | 0.79697
2018-03-30 | 0.082467 | 0 | 0 | 0 | 0.068302 | 0.059829 | 0.39324
2018-03-31 | 0.079059 | 0 | 0 | 0 | 0.063697 | 0.059829 | 0.083868
2018-04-01 | 0.079578 | 0 | 0 | 0 | 0.06965 | 0.060052 | 0.085019
2018-04-01 23:00 | 0.068262 | 0 | 0 | 0 | 0.067361 | 0.059829 | 0.071526
2018-04-02 23:00 | 0.076598 | 0 | 0 | 0 | 0.10949 | 0.097701 | 0.075141
2018-04-03 23:00 | 0.076581 | 0 | 0 | 0 | 0.08299 | 0.06585 | 0.074687
2018-04-04 23:00 | 0.082761 | 0 | 0.16019 | 0.16093 | 0.29308 | 0.29538 | 0.47318
2018-04-05 23:00 | 0.25418 | 0 | 0.48786 | 0.48741 | 0.67149 | 0.73682 | 0.79648
2018-04-06 23:00 | 0.25937 | 0 | 0.42878 | 0.46778 | 0.70317 | 0.78679 | 0.81108
2018-04-07 23:00 | 0.24684 | 0 | 0.52718 | 0.53902 | 0.68463 | 0.78049 | 0.81507
2018-04-08 23:00 | 0.26024 | 0 | 0.33495 | 0.3888 | 0.68473 | 0.77689 | 0.79562
2018-04-09 23:00 | 0.13222 | 0 | 0.65901 | 0.69637 | 0.7957 | 0.89928 | 0.78945
2018-04-10 23:00 | 0.084426 | 0 | 0.58377 | 0.60317 | 0.87503 | 0.96086 | 0.31513
2018-04-11 23:00 | 0.08328 | 0 | 0.68649 | 0.70892 | 0.71856 | 0.85007 | 0.29936
2018-04-12 23:00 | 0.090685 | 0 | 0.61373 | 0.64209 | 0.4242 | 0.50524 | 0.4952
2018-04-13 23:00 | 0.085933 | 0 | 0.65707 | 0.64952 | 0.049611 | 0.057555 | 0.81653
2018-04-14 23:00 | 0.082879 | 0 | 0.20634 | 0.15203 | 0.050394 | 0.059829 | 0.60307
2018-04-15 23:00 | 0.074383 | 0 | 0.32501 | 0.38514 | 0.26369 | 0.31644 | 0.12939
2018-04-16 23:00 | 0.26704 | 0 | 0.65699 | 0.6652 | 0.69341 | 0.77418 | 0.071701
2018-04-17 23:00 | 0.27571 | 0 | 0.31502 | 0.35394 | 0.65238 | 0.69864 | 0.078779
2018-04-18 23:00 | 0.28627 | 0 | 0.042819 | 0.12514 | 0.5966 | 0.63219 | 0.073543
2018-04-19 23:00 | 0.38924 | 0 | 0.063359 | 0.066522 | 0.6919 | 0.73601 | 0.3629
2018-04-20 23:00 | 0.32958 | 0 | 0.052587 | 0.054539 | 0.68337 | 0.7379 | 0.79296
2018-04-21 23:00 | 0.27154 | 0 | 0.053059 | 0.054129 | 0.67427 | 0.73682 | 0.79036
2018-04-22 23:00 | 0.22634 | 0 | 0.3231 | 0.35079 | 0.2446 | 0.25958 | 0.78819
2018-04-23 23:00 | 0.083733 | 0 | 0.69752 | 0.66228 | 0.25849 | 0.27291 | 0.79383
2018-04-24 23:00 | 0.22717 | 0 | 0.13599 | 0.098477 | 0.66224 | 0.72638 | 0.82048
2018-04-25 23:00 | 0.25045 | 0 | 0.38888 | 0.42859 | 0.67416 | 0.73052 | 0.80238
2018-04-26 23:00 | 0.32644 | 0 | 0.70737 | 0.68548 | 0.67536 | 0.73758 | 0.75823
2018-04-27 23:00 | 0.22991 | 0 | 0.69844 | 0.71597 | 0.67008 | 0.73647 | 0.81992
2018-04-28 23:00 | 0.14286 | 0 | 0.66759 | 0.65684 | 0.60127 | 0.66063 | 0.81007
2018-04-29 23:00 | 0.11075 | 0 | 0.76116 | 0.75035 | 0.63994 | 0.70876 | 0.80874
2018-04-30 23:00 | 0.26101 | 0 | 0.81081 | 0.71002 | 0.65353 | 0.73092 | 0.83128
2018-05-01 23:00 | 0.29182 | 0 | 0.84069 | 0.73714 | 0.63771 | 0.71798 | 0.83135
2018-05-02 23:00 | 0.281 | 0 | 0.84323 | 0.72549 | 0.47563 | 0.52165 | 0.81451
2018-05-03 23:00 | 0.12414 | 0 | 0.85628 | 0.72687 | 0.18145 | 0.12866 | 0.83679
2018-05-04 23:00 | 0.087388 | 0 | 0.32989 | 0.2141 | 0.069068 | 0.047077 | 0.82272
2018-05-05 23:00 | 0.087962 | 0 | 0.066849 | 0.063269 | 0.070386 | 0.050082 | 0.8254
2018-05-06 23:00 | 0.13623 | 0 | 0.47677 | 0.46722 | 0.60298 | 0.46132 | 0.82921
2018-05-07 23:00 | 0.27376 | 0 | 0.83009 | 0.72284 | 0.92593 | 0.7188 | 0.80824
2018-05-08 23:00 | 0.27048 | 0 | 0.83793 | 0.7542 | 0.8439 | 0.7236 | 0.81154
2018-05-09 23:00 | 0.28368 | 0 | 0.43942 | 0.41693 | 0.7888 | 0.72513 | 0.82019
2018-05-10 23:00 | 0.27954 | 0 | 0.2182 | 0.12554 | 0.76847 | 0.73691 | 0.80827
2018-05-11 23:00 | 0.2321 | 0 | 0.068277 | 0.065893 | 0.78297 | 0.73839 | 0.82418
2018-05-12 23:00 | 0.19693 | 0 | 0.059242 | 0.056486 | 0.18507 | 0.17125 | 0.82564
2018-05-13 23:00 | 0.21494 | 0 | 0.045818 | 0.046946 | 0.4 | 0.38186 | 0.82933
2018-05-14 23:00 | 0.67095 | 0 | 0.043777 | 0.046217 | 0.73552 | 0.71135 | 0.81782
2018-05-15 23:00 | 0.66856 | 0 | 0.046937 | 0.048869 | 0.70988 | 0.69822 | 0.81386
2018-05-16 23:00 | 0.6679 | 0 | 0.048951 | 0.050727 | 0.67838 | 0.68513 | 0.72331
2018-05-17 23:00 | 0.66632 | 0 | 0.046438 | 0.047598 | 0.66761 | 0.68142 | 0.79854
2018-05-18 23:00 | 0.67807 | 0 | 0.047056 | 0.048756 | 0.67308 | 0.70294 | 0.81471
2018-05-19 23:00 | 0.67713 | 0 | 0.050795 | 0.052029 | 0.68108 | 0.70707 | 0.81981
2018-05-20 23:00 | 0.68479 | 0 | 0.052467 | 0.053243 | 0.68676 | 0.7299 | 0.81238
2018-05-21 23:00 | 0.58164 | 0 | 0.051018 | 0.10954 | 0.35026 | 0.3669 | 0.81887
2018-05-22 23:00 | 0.6547 | 0 | 0.046443 | 0.048423 | 0.86809 | 0.91356 | 0.81115
2018-05-23 23:00 | 0.60588 | 0 | 0.04363 | 0.048904 | 0.84994 | 0.89493 | 0.81301
2018-05-24 23:00 | 0.49899 | 0 | 0.039418 | 0.048922 | 0.62942 | 0.68714 | 0.8082
2018-05-25 23:00 | 0.66941 | 0 | 0.040279 | 0.048952 | 0.62382 | 0.68406 | 0.8219
2018-05-26 23:00 | 0.66579 | 0 | 0.0417 | 0.048955 | 0.61792 | 0.67838 | 0.82057
2018-05-27 23:00 | 0.6673 | 0 | 0.042181 | 0.049028 | 0.22717 | 0.24588 | 0.82284
2018-05-28 23:00 | 0.53111 | 0 | 0.040188 | 0.70753 | 0.091307 | 0.096649 | 0.84386
2018-05-29 23:00 | 0.4647 | 0 | 0.037732 | 0.045119 | 0.26557 | 0.29544 | 0.60395
2018-05-30 23:00 | 0.6625 | 0 | 0.049169 | 0.04516 | 0.5988 | 0.67927 | 0.7358
2018-05-31 23:00 | 0.66463 | 0 | 0.044081 | 0.045081 | 0.64698 | 0.68638 | 0.83561
2018-06-01 23:00 | 0.66831 | 0 | 0.047413 | 0.045034 | 0.67184 | 0.70356 | 0.83416
2018-06-02 23:00 | 0.66572 | 0 | 0.050788 | 0.17094 | 0.3884 | 0.40919 | 0.84136
2018-06-03 23:00 | 0.49481 | 0 | 0.053774 | 0.29122 | 0.065997 | 0.071464 | 0.83351
2018-06-04 23:00 | 0.42297 | 0 | 0.055039 | 0.044924 | 0.05872 | 0.063443 | 0.67454
2018-06-05 23:00 | 0.28041 | 0 | 0.053264 | 0.04507 | 0.021488 | 0.0483 | 0.23447
2018-06-06 23:00 | 0.079654 | 0 | 0.072642 | 0.05005 | 0.01065 | 0.039372 | 0.42238
2018-06-07 23:00 | 0.19963 | 0 | 0.39955 | 0.40069 | 0.015809 | 0.046089 | 0.50667
2018-06-08 23:00 | 0.63162 | 0 | 0.86498 | 0.72595 | 0.032384 | 0.036476 | 0.080896
2018-06-09 23:00 | 0.60619 | 0 | 0.83054 | 0.69535 | 0.049667 | 0.047231 | 0.081953
2018-06-10 23:00 | 0.5698 | 0 | 0.66003 | 0.51484 | 0.043087 | 0.047396 | 0.081404
2018-06-11 23:00 | 0.49533 | 0 | 0.27729 | 0.25735 | 0.041719 | 0.041441 | 0.076677
2018-06-12 23:00 | 0.5995 | 0 | 0.2771 | 0.22715 | 0.054822 | 0.049844 | 0.077916
2018-06-13 23:00 | 0.4485 | 0 | 0.38773 | 0.41375 | 0.031027 | 0.03428 | 0.076833
2018-06-14 23:00 | 0.42909 | 0 | 0.76102 | 0.7095 | 0.13086 | 0.31971 | 0.46149
2018-06-15 23:00 | 0.65974 | 0 | 0.66155 | 0.71523 | 0 | 0.68923 | 0.83706
2018-06-16 23:00 | 0.65641 | 0 | 0.64933 | 0.69877 | 0 | 0.62876 | 0.82253
2018-06-17 23:00 | 0.59485 | 0 | 0.68442 | 0.74913 | 0.80287 | 0.72308 | 0.81004
2018-06-18 23:00 | 0.64603 | 0 | 0.67476 | 0.74517 | 1.4496 | 0.68837 | 0.82394
2018-06-19 23:00 | 0.63136 | 0 | 0.67742 | 0.70774 | 0.53413 | 0.67354 | 0.82673
2018-06-20 23:00 | 0.66375 | 0 | 0.65112 | 1.4577 | 1.0756 | 0.6865 | 0.78845
2018-06-21 23:00 | 0.66121 | 0 | 0.060915 | 0.90083 | 0.55187 | 0.68254 | 0.82127
2018-06-22 23:00 | 0.66121 | 0 | 0.031613 | 0.057586 | 0.61565 | 0.68819 | 0.75263
2018-06-23 23:00 | 0.66467 | 0 | 0.033897 | 0.059953 | 0.92634 | 0.68232 | 0.83405
2018-06-24 23:00 | 0.34547 | 0 | 0.03297 | 0.057796 | 0.93452 | 0.6837 | 0.82713
2018-06-25 23:00 | 0.37519 | 0 | 0.028811 | 0.056756 | 0.52649 | 0.67567 | 0.82146
2018-06-26 23:00 | 0.31735 | 0 | 0.31456 | 0.407 | 0.57739 | 0.66584 | 0.83579
2018-06-27 23:00 | 0.32485 | 0 | 0.65698 | 0.68328 | 0.8133 | 0.65823 | 0.84119
2018-06-28 23:00 | 0.31711 | 0 | 0.66396 | 0.68626 | 0.48961 | 0.45155 | 0.84057
2018-06-29 23:00 | 0.092157 | 0 | 0.65808 | 0.69682 | 0.050287 | 0.052428 | 0.73311
2018-06-30 23:00 | 0.074647 | 0 | 0.65948 | 0.70373 | 0.062792 | 0.050541 | 0.085206

## 18-19
Date Stamp | .Gear Island 1050 Fluoride | .Gear Island 1050 Fluoride Analyser #2 | .Te Marua PS Fluoride Residual | .Te Marua TP Fluoride Residual | .Wainui Fluoride Building Fluoride Residual Stream 1 | .Wainui Fluoride Building Fluoride Residual Stream 2 | .Waterloo Naenae Fluoride Residual
2018-07-01 23:00 | 0.07588 | 0 | 0.65197 | 0.70832 | 0.07265 | 0.049654 | 0.32787
2018-07-02 23:00 | 0.076152 | 0 | 0.64753 | 0.68481 | 0.048169 | 0.050027 | 0.82436
2018-07-03 23:00 | 0.080302 | 0 | 0.64736 | 0.68966 | 0.052057 | 0.050015 | 0.82991
2018-07-04 23:00 | 0.12058 | 0 | 0.65938 | 0.68925 | 0.27264 | 0.1837 | 0.57091
2018-07-05 23:00 | 0.08201 | 0 | 0.65721 | 0.69629 | 0.17805 | 0.042625 | 0.50289 |  | Analysers not installed or was off
2018-07-06 23:00 | 0.081376 | 0 | 0.65467 | 0.71756 | 0.20548 | 0.048624 | 0.8222 |  | Fluoride not dosed
2018-07-07 23:00 | 0.087851 | 0 | 0.66336 | 0.72022 | 0.27931 | 0.065719 | 0.82206 |  | fluoride dosed but outside recommended range
2018-07-08 23:00 | 0.087877 | 0 | 0.68787 | 0.74171 | 0.56341 | 0.12922 | 0.80872 |  | Fluoride dosed but within recommended range
2018-07-09 23:00 | 0.083061 | 0 | 0.67231 | 0.76743 | 0.45107 | 0.11399 | 0.77502
2018-07-10 23:00 | 0.1774 | 0 | 0.66869 | 0.73916 | 0.74139 | 0.44019 | 0.83483 | Assumptions: |  | 1. Values less than 0.1 indicates that fluoride is not being dosed
2018-07-11 23:00 | 0.44457 | 0 | 0.61973 | 0.65706 | 0.92734 | 0.70254 | 0.5179 |  |  | 2. MAV exceedences at the Te Marua PS are due to the default value that the analyser goes to when fluoride dosing is ceased
2018-07-12 23:00 | 0.29924 | 0 | 0.6207 | 0.67779 | 0.66265 | 0.69474 | 0.58324 |  |  | 3. The Gear Island sampling point is downstream of the plant and can contain a residual from the Wainuiomata WTP
2018-07-13 23:00 | 0.24588 | 0 | 0.67838 | 0.74121 | 0.68455 | 0.68453 | 0.905
2018-07-14 23:00 | 0.21753 | 0 | 0.27998 | 0.26218 | 0.64652 | 0.67626 | 0.62551
2018-07-15 23:00 | 0.24004 | 0 | 0.38023 | 0.48899 | 0.67868 | 0.68515 | 0.89626
2018-07-16 23:00 | 0.25459 | 0 | 0.66126 | 0.714 | 0.72807 | 0.68741 | 0.9108
2018-07-17 23:00 | 0.32949 | 0 | 0.72822 | 0.7247 | 0.75582 | 0.69372 | 0.76736
2018-07-18 23:00 | 0.28698 | 0 | 0.69749 | 0.64993 | 0.73948 | 0.67931 | 0.90526
2018-07-19 23:00 | 0.26638 | 0 | 0.77875 | 0.72407 | 0.74005 | 0.67699 | 0.49767
2018-07-20 23:00 | 0.27586 | 0 | 0.78276 | 0.73104 | 0.75771 | 0.67193 | 0.91161
2018-07-21 23:00 | 0.24193 | 0 | 0.76132 | 0.74372 | 0.77464 | 0.66844 | 0.919
2018-07-22 23:00 | 0.13771 | 0 | 0.78438 | 0.72305 | 0.66304 | 0.53873 | 0.90734
2018-07-23 23:00 | 0.28517 | 0 | 0.79121 | 0.74434 | 0.82573 | 0.67336 | 0.89137
2018-07-24 23:00 | 0.34635 | 0 | 0.74881 | 0.68422 | 0.83589 | 0.71174 | 0.88089
2018-07-25 23:00 | 0.19679 | 0 | 0.72613 | 1.2733 | 0.32261 | 0.26704 | 0.86931
2018-07-26 23:00 | 0.18992 | 0 | 0.12634 | 0.082986 | 0.49213 | 0.46847 | 0.87102
2018-07-27 23:00 | 0.28588 | 0 | 0.042551 | 0.057092 | 0.71319 | 0.73743 | 0.86554
2018-07-28 23:00 | 0.30312 | 0 | 0.044297 | 0.058851 | 0.72539 | 0.7417 | 0.86894
2018-07-29 23:00 | 0.31087 | 0 | 0.24399 | 0.26804 | 0.73911 | 0.74238 | 0.86987
2018-07-30 23:00 | 0.29831 | 0 | 0.7085 | 1.1056 | 0.73603 | 0.79838 | 0.87356
2018-07-31 23:00 | 0.33369 | 0 | 0.073317 | 0.60241 | 0.72382 | 0.80622 | 0.86362
2018-08-01 23:00 | 0.29636 | 0 | 0.048426 | 0.061671 | 0.71016 | 0.79216 | 0.86548
2018-08-02 23:00 | 0.33767 | 0 | 0.045707 | 0.058659 | 0.72188 | 0.79619 | 0.4262
2018-08-03 23:00 | 0.31454 | 0 | 0.041355 | 0.054907 | 0.72987 | 0.78719 | 0.86378
2018-08-04 23:00 | 0.27359 | 0 | 0.039395 | 0.053479 | 0.74154 | 0.80222 | 0.86535
2018-08-05 23:00 | 0.28569 | 0 | 0.039762 | 0.053681 | 0.75547 | 0.80442 | 0.87706
2018-08-06 23:00 | 0.30939 | 0 | 0.048745 | 0.85252 | 0.8075 | 0.80364 | 0.85485
2018-08-07 23:00 | 0.35131 | 0 | 0.042804 | 0.059744 | 0.78568 | 0.77066 | 0.87083
2018-08-08 23:00 | 0.27563 | 0 | 0.13848 | 0.13288 | 0.80877 | 0.78323 | 0.71342
2018-08-09 23:00 | 0.29345 | 0 | 0.40449 | 0.43778 | 0.77408 | 0.75206 | 0.87958
2018-08-10 23:00 | 0.28079 | 0 | 0.72568 | 0.67004 | 0.80661 | 0.7941 | 0.87853
2018-08-11 23:00 | 0.29577 | 0 | 0.13713 | 0.11421 | 0.823 | 0.79605 | 0.8728
2018-08-12 23:00 | 0.30178 | 0 | 0.1561 | 0.1642 | 0.83605 | 0.79025 | 0.8652
2018-08-13 23:00 | 0.32875 | 0 | 0.044331 | 1.0785 | 0.86246 | 0.81137 | 0.88182
2018-08-14 23:00 | 0.28243 | 0 | 0.045768 | 0.063099 | 0.83817 | 0.79583 | 0.87305
2018-08-15 23:00 | 0.29076 | 0 | 0.04565 | 0.058151 | 0.80421 | 0.78266 | 0.86514
2018-08-16 23:00 | 0.33047 | 0 | 0.042337 | 0.05502 | 0.81725 | 0.78675 | 0.8556
2018-08-17 23:00 | 0.24402 | 0 | 0.037316 | 0.050328 | 0.8729 | 0.78225 | 0.87357
2018-08-18 23:00 | 0.22322 | 0 | 0.032408 | 0.046437 | 0.8783 | 0.77548 | 0.88239
2018-08-19 23:00 | 0.30752 | 0 | 0.032997 | 0.046749 | 0.89127 | 0.8025 | 0.8914
2018-08-20 23:00 | 0.26462 | 0 | 0.038751 | 0.05206 | 0.89299 | 0.88143 | 0.89291
2018-08-21 23:00 | 0.25859 | 0 | 0.047979 | 0.061702 | 0.79224 | 0.88332 | 0.87473
2018-08-22 23:00 | 0.25435 | 0 | 0.03633 | 0.048153 | 0.65896 | 0.88714 | 0.87903
2018-08-23 23:00 | 0.27608 | 0 | 0.041182 | 0.052468 | 0.76174 | 0.89039 | 0.88008
2018-08-24 23:00 | 0.32227 | 0 | 0.028524 | 0.041371 | 0.76599 | 0.89816 | 0.87007
2018-08-25 23:00 | 0.31851 | 0 | 0.029776 | 0.04291 | 0.78166 | 0.91446 | 0.88784
2018-08-26 23:00 | 0.34616 | 0 | 0.33942 | 0.3452 | 0.81087 | 0.93118 | 0.89554
2018-08-27 23:00 | 0.38095 | 0 | 0.73206 | 0.69626 | 0.79604 | 0.8654 | 0.87898
2018-08-28 23:00 | 0.3481 | 0 | 0.74912 | 0.69904 | 0.80034 | 0.79378 | 0.8783
2018-08-29 23:00 | 0.35864 | 0 | 0.7461 | 0.71256 | 0.82427 | 0.79478 | 0.86815
2018-08-30 23:00 | 0.29658 | 0 | 0.75577 | 0.70236 | 0.82125 | 0.7595 | 0.87051
2018-08-31 23:00 | 0.24238 | 0 | 0.75996 | 0.70392 | 0.76456 | 0.76186 | 0.86233
2018-09-01 23:00 | 0.26478 | 0 | 0.74958 | 0.6992 | 0.71111 | 0.77758 | 0.87254
2018-09-02 23:00 | 0.1122 | 0 | 0.75579 | 0.70412 | 0.71776 | 0.7505 | 0.6615
2018-09-03 23:00 | 0.087442 | 0 | 0.56521 | 0.47948 | 0.83015 | 0.88141 | 0.45954
2018-09-04 23:00 | 0.12124 | 0 | 0.32466 | 0.38611 | 0.68524 | 0.70812 | 0.86974
2018-09-05 23:00 | 0.43928 | 0 | 0.77848 | 0.70997 | 0.70728 | 0.74338 | 0.60646
2018-09-06 23:00 | 0.33683 | 0 | 0.78156 | 0.70027 | 0.71333 | 0.74501 | 0.86796
2018-09-07 23:00 | 0.32782 | 0 | 0.75549 | 0.67024 | 0.70581 | 0.75057 | 0.85857
2018-09-08 23:00 | 0.3699 | 0 | 0.77229 | 0.69923 | 0.6922 | 0.74701 | 0.80911
2018-09-09 23:00 | 0.36175 | 0 | 0.75087 | 0.68241 | 0.68261 | 0.74424 | 0.87491
2018-09-10 23:00 | 0.38309 | 0 | 0.75919 | 0.69199 | 0.7115 | 0.74116 | 1.032
2018-09-11 23:00 | 0.42604 | 0 | 0.78075 | 0.7139 | 0.72634 | 0.72024 | 0.8695
2018-09-12 23:00 | 0.42179 | 0 | 0.51632 | 0.43679 | 0.80616 | 0.74718 | 0.87479
2018-09-13 23:00 | 0.35634 | 0 | 0.25953 | 0.26698 | 0.8442 | 0.76351 | 0.87482
2018-09-14 23:00 | 0.34835 | 0 | 0.045476 | 0.057758 | 0.8571 | 0.76242 | 0.8777
2018-09-15 23:00 | 0.35336 | 0 | 0.046325 | 0.058367 | 0.86491 | 0.76303 | 0.87137
2018-09-16 23:00 | 0.36687 | 0 | 0.43383 | 0.46794 | 0.88942 | 0.77554 | 0.88895
2018-09-17 23:00 | 0.22201 | 0 | 0.29391 | 0.27703 | 0.63612 | 0.53755 | 1.3617
2018-09-18 23:00 | 0.096152 | 0 | 0.24742 | 0.28311 | 0.56916 | 0.45597 | 0.8735
2018-09-19 23:00 | 0.096832 | 0 | 0.37121 | 0.37694 | 0.68488 | 0.55747 | 0.57897
2018-09-20 23:00 | 0.088245 | 0 | 0.30755 | 0.34069 | 0.87454 | 0.72497 | 0.59316
2018-09-21 23:00 | 0.090978 | 0 | 0.74265 | 0.6998 | 0.87454 | 0.72497 | 0.88917
2018-09-22 23:00 | 0.091258 | 0 | 0.7482 | 0.71848 | 0.87454 | 0.72497 | 0.88746
2018-09-23 23:00 | 0.091325 | 0 | 0.71631 | 0.70481 | 0.87454 | 0.72497 | 0.88721
2018-09-24 23:00 | 0.091527 | 0 | 0.73808 | 0.71459 | 0.87454 | 0.72497 | 0.88664
2018-09-25 23:00 | 0.090158 | 0 | 0.50797 | 0.46446 | 0.87454 | 0.72497 | 0.88411
2018-09-26 23:00 | 0.092111 | 0 | 0.51299 | 0.48731 | 0.75562 | 0.61861 | 0.87919
2018-09-27 23:00 | 0.092031 | 0 | 0.74048 | 0.7211 | 0.51805 | 0.44839 | 0.88776
2018-09-28 23:00 | 0.090787 | 0 | 0.7574 | 0.7317 | 0.43796 | 0.47251 | 0.88265
2018-09-29 23:00 | 0.092567 | 0 | 0.74297 | 0.7197 | 0.50527 | 0.55059 | 0.88803
2018-10-01 | 0.091882 | 0 | 0.75362 | 0.74959 | 0.52292 | 0.55875 | 0.88662
2018-10-02 | 0.092019 | 0 | 0.74348 | 0.72035 | 0.52495 | 0.57606 | 0.54015
2018-10-03 | 0.097129 | 0 | 0.75354 | 0.74218 | 0.36029 | 0.39737 | 0.89165
2018-10-04 | 0.087074 | 0 | 0.75613 | 0.7238 | 0.1907 | 0.20327 | 0.75589
2018-10-05 | 0.089687 | 0 | 0.74606 | 0.72354 | 0.07706 | 0.077884 | 0.88979
2018-10-06 | 0.088792 | 0 | 0.75161 | 0.71999 | 0.055977 | 0.059257 | 0.88578
2018-10-07 | 0.088957 | 0 | 0.74946 | 0.7113 | 0.063722 | 0.069253 | 0.88944
2018-10-08 | 0.096951 | 0 | 0.74854 | 0.73359 | 0.058031 | 0.061034 | 0.89096
2018-10-09 | 0.099007 | 0 | 0.66867 | 0.73518 | 0.050504 | 0.050823 | 0.89151
2018-10-10 | 0.24375 | 0 | 0.4281 | 0.56658 | 0.43507 | 0.50864 | 0.89324
2018-10-11 | 0.34114 | 0 | 0.65498 | 0.75486 | 0.50068 | 0.5816 | 0.90161
2018-10-12 | 0.095065 | 0 | 0.8377 | 0.74445 | 0.38144 | 0.42253 | 0.88691
2018-10-13 | 0.090267 | 0 | 0.83787 | 0.74573 | 0.11802 | 0.11793 | 0.88583
2018-10-14 | 0.090685 | 0 | 0.84921 | 0.70253 | 0.12731 | 0.12961 | 0.88441
2018-10-15 | 0.090942 | 0 | 0.86283 | 0.73375 | 0.33049 | 0.3526 | 0.37737
2018-10-16 | 0.31827 | 0 | 0.85113 | 0.73564 | 0.65099 | 0.69719 | 0.31912
2018-10-17 | 0.34317 | 0 | 0.83915 | 0.72864 | 0.65523 | 0.70234 | 0.080138
2018-10-18 | 0.29583 | 0 | 0.86044 | 0.73968 | 0.61327 | 0.64377 | 0.086173
2018-10-19 | 0.29255 | 0 | 0.84242 | 0.72401 | 0.66225 | 0.69425 | 0.087776
2018-10-20 | 0.33502 | 0 | 0.75229 | 0.6034 | 0.65715 | 0.69837 | 0.085113
2018-10-21 | 0.47177 | 0 | 0.10421 | 0.065876 | 0.65294 | 0.69734 | 0.091776
2018-10-22 | 0.34886 | 0 | 0.066921 | 0.065632 | 0.64764 | 0.69344 | 0.088161
2018-10-23 | 0.33757 | 0 | 0.49766 | 0.49005 | 0.65488 | 0.68631 | 0.085755
2018-10-24 | 0.34529 | 0 | 0.84719 | 0.73746 | 0.64874 | 0.68984 | 0.084058
2018-10-25 | 0.35033 | 0 | 0.86248 | 0.73725 | 0.70187 | 0.72267 | 0.08065
2018-10-26 | 0.33809 | 0 | 0.85574 | 0.72934 | 0.74628 | 0.72839 | 0.089456
2018-10-27 | 0.31832 | 0 | 0.37213 | 0.24809 | 0.75621 | 0.73607 | 0.07589
2018-10-28 | 0.23907 | 0 | 0.41867 | 0.38756 | 0.64452 | 0.62195 | 0.078633
2018-10-29 | 0.14873 | 0 | 0.71531 | 0.5737 | 0.064877 | 0.0504 | 0.077379
2018-10-30 | 0.081737 | 0 | 0.85712 | 0.71782 | 0.057907 | 0.050926 | 0.078338
2018-10-31 | 0.083724 | 0 | 0.70867 | 0.55712 | 0.072484 | 0.066354 | 0.078485
2018-11-01 | 0.097427 | 0 | 0.52336 | 0.48358 | 0.47865 | 0.44016 | 0.081882
2018-11-02 | 0.31242 | 0 | 0.85652 | 0.73016 | 0.79959 | 0.71483 | 0.083483
2018-11-03 | 0.28968 | 0 | 0.88561 | 0.73017 | 0.8127 | 0.73046 | 0.082388
2018-11-04 | 0.23303 | 0 | 0.85025 | 0.72167 | 0.82376 | 0.71409 | 0.083979
2018-11-05 | 0.30154 | 0 | 0.8731 | 0.73629 | 0.85543 | 0.71576 | 0.082651
2018-11-06 | 0.30039 | 0 | 0.82629 | 0.72328 | 0.86195 | 0.72011 | 0.083573
2018-11-07 | 0.30234 | 0 | 0.68586 | 0.58718 | 0.82848 | 0.75525 | 0.085291
2018-11-08 | 0.26987 | 0 | 0.059302 | 2.0597 | 0.7814 | 0.81114 | 0.09765
2018-11-09 | 0.22676 | 0 | 0.081496 | 0.096037 | 0.72898 | 0.73977 | 0.082506
2018-11-10 | 0.088537 | 0 | 0.054763 | 0.058293 | 0.87277 | 0.87752 | 0.082449
2018-11-11 | 0.086366 | 0 | 0.048486 | 0.052845 | 0.72067 | 0.71457 | 0.082153
2018-11-12 | 0.14776 | 0 | 0.045128 | 0.049396 | 0.70332 | 0.6874 | 0.081569
2018-11-13 | 0.46275 | 0 | 0.29852 | 0.30382 | 0.86188 | 0.83266 | 0.077477
2018-11-14 | 0.34038 | 0 | 0.69323 | 1.8854 | 0.85124 | 0.83361 | 0.08452
2018-11-15 | 0.38308 | 0 | 0.50626 | 0.51197 | 0.81951 | 0.81911 | 0.085544
2018-11-16 | 0.34595 | 0 | 0.81334 | 0.71381 | 0.79402 | 0.80399 | 0.085129
2018-11-17 | 0.31855 | 0 | 0.82747 | 0.72517 | 0.79307 | 0.80654 | 0.088397
2018-11-18 | 0.30766 | 0 | 0.80887 | 0.71388 | 0.78648 | 0.80108 | 0.086256
2018-11-19 | 0.31073 | 0 | 0.83032 | 0.72419 | 0.78016 | 0.79398 | 0.081656
2018-11-20 | 0.33036 | 0 | 0.84359 | 0.67913 | 0.77068 | 0.79069 | 0.07378
2018-11-21 | 0.31123 | 0 | 0.91035 | 0.72018 | 0.78954 | 0.78889 | 0.097689
2018-11-22 | 0.23956 | 0 | 0.90464 | 0.71386 | 0.62768 | 0.63275 | 0.077466
2018-11-23 | 0.281 | 0 | 0.83787 | 0.72264 | 0.80754 | 0.80395 | 0.077833
2018-11-24 | 0.31444 | 0 | 0.72797 | 0.72907 | 0.77488 | 0.76437 | 0.079733
2018-11-25 | 0.33433 | 0 | 0.72309 | 0.72074 | 0.77682 | 0.78168 | 0.078288
2018-11-26 | 0.16087 | 0 | 0.71436 | 0.7352 | 0.55387 | 0.56046 | 0.080655
2018-11-27 | 0.099728 | 0 | 0.71717 | 0.74925 | 0.20929 | 0.20675 | 0.077972
2018-11-28 | 0.083989 | 0 | 0.71343 | 0.73122 | 0.18112 | 0.17451 | 0.07755
2018-11-29 | 0.087238 | 0 | 0.73864 | 0.73191 | 0.32846 | 0.32292 | 0.077107
2018-11-30 | 0.29928 | 0 | 0.72448 | 0.71192 | 0.78166 | 0.7708 | 0.077666
2018-12-01 | 0.27088 | 0 | 0.73889 | 0.74275 | 0.78271 | 0.77576 | 0.07747
2018-12-02 | 0.29654 | 0 | 0.73199 | 0.73026 | 0.78857 | 0.78281 | 0.077886
2018-12-03 | 0.30654 | 0 | 0.73091 | 0.72888 | 0.72642 | 0.71631 | 0.077873
2018-12-04 | 0.2612 | 0 | 0.72503 | 0.73548 | 0.77331 | 0.77299 | 0.076406
2018-12-05 | 0.31974 | 0 | 0.54554 | 0.50282 | 0.75027 | 0.76411 | 0.077542
2018-12-06 | 0.36571 | 0 | 0.43917 | 0.53623 | 0.75847 | 0.7699 | 0.077285
2018-12-07 | 0.288 | 0 | 0.73266 | 0.74589 | 0.52386 | 0.52201 | 0.077747
2018-12-08 | 0.28437 | 0 | 0.76731 | 0.73753 | 0.78642 | 0.76466 | 0.076567
2018-12-09 | 0.31893 | 0 | 0.75838 | 0.74393 | 0.7888 | 0.75563 | 0.076367
2018-12-10 | 0.31906 | 0 | 0.75682 | 0.73953 | 0.78653 | 0.75109 | 0.076854
2018-12-11 | 0.31911 | 0 | 0.76615 | 0.72528 | 0.77836 | 0.76186 | 0.08635
2018-12-12 | 0.32545 | 0 | 0.75795 | 0.7422 | 0.73223 | 0.73086 | 0.094554
2018-12-13 | 0.3082 | 0 | 0.76514 | 0.74958 | 0.7092 | 0.70544 | 0.077095
2018-12-14 | 0.36834 | 0 | 0.75301 | 0.74658 | 0.76263 | 0.75355 | 0.077887
2018-12-15 | 0.27048 | 0 | 0.77856 | 0.74421 | 0.75909 | 0.76053 | 0.081013
2018-12-16 | 0.33471 | 0 | 0.77179 | 0.73266 | 0.75235 | 0.76601 | 0.07689
2018-12-17 | 0.42116 | 0 | 0.78577 | 0.71935 | 0.75895 | 0.78585 | 0.31647
2018-12-18 | 0.35858 | 0 | 0.78453 | 0.73875 | 0.76987 | 0.78649 | 0.49316
2018-12-19 | 0.35359 | 0 | 0.79061 | 0.72451 | 0.77418 | 0.75065 | 0.72206
2018-12-20 | 0.10071 | 0 | 0.81203 | 0.74936 | 0.83345 | 0.74023 | 0.55499
2018-12-21 | 0.14881 | 0 | 0.85309 | 0.7534 | 0.73148 | 0.6378 | 0.60662
2018-12-22 | 0.26154 | 0 | 0.8594 | 0.72516 | 0.82246 | 0.70359 | 0.66513
2018-12-23 | 0.30303 | 0 | 0.86201 | 0.73797 | 0.80865 | 0.70514 | 0.079207
2018-12-24 | 0.30927 | 0 | 0.83958 | 0.70131 | 0.80984 | 0.71117 | 0.44513
2018-12-25 | 0.26565 | 0 | 0.81511 | 0.70726 | 0.56397 | 0.5039 | 0.8448
2018-12-26 | 0.091945 | 0 | 0.77943 | 0.6233 | 0.18253 | 0.14945 | 0.84677
2018-12-27 | 0.13746 | 0 | 0.39023 | 0.34249 | 0.55446 | 0.46297 | 0.84869
2018-12-28 | 0.30072 | 0 | 0.81079 | 0.67912 | 0.86303 | 0.73845 | 0.84192
2018-12-29 | 0.3677 | 0 | 0.1478 | 0.093427 | 0.8703 | 0.73337 | 0.099837
2018-12-30 | 0.29292 | 0 | 0.068884 | 0.061049 | 0.63735 | 0.55099 | 0.083745
2018-12-31 | 0.12756 | 0 | 0.23041 | 0.19129 | 0.074753 | 0.059106 | 0.085756
2019-01-01 | 0.087699 | 0 | 0.081141 | 0.063252 | 0.070882 | 0.062266 | 0.20865
2019-01-02 | 0.086105 | 0 | 0.1171 | 0.063305 | 0.070882 | 0.068697 | 0.083584
2019-01-03 | 0.0844 | 0 | 0.40843 | 0.22287 | 0.070882 | 0.070563 | 0.57548
2019-01-04 | 0.086539 | 0 | 0.27543 | 0.14832 | 0.072677 | 0.057535 | 0.84474
2019-01-05 | 0.08125 | 0 | 0.20318 | 0.063261 | 0.064432 | 0.052457 | 0.14501
2019-01-06 | 0.080454 | 0 | 0.46175 | 0.064543 | 0.073692 | 0.057026 | 0.083649
2019-01-07 | 0.087109 | 0 | 0.82916 | 0.064195 | 0.080876 | 0.069652 | 0.67573
2019-01-08 | 0.088739 | 0 | 0.59651 | 0.21238 | 0.073904 | 0.060234 | 0.85275
2019-01-09 | 0.094959 | 0 | 0.27512 | 0.23194 | 0.079606 | 0.075105 | 0.79009
2019-01-10 | 0.087453 | 0 | 0.23171 | 0.16675 | 0.074786 | 0.06718 | 4.4854 | MAV Exceeded
2019-01-11 | 0.12727 | 0 | 0.19379 | 0.13202 | 0.53975 | 0.47617 | 4.2798 | MAV Exceeded
2019-01-12 | 0.25526 | 0 | 0.10804 | 0.064044 | 0.8371 | 0.74951 | 4.2744 | MAV Exceeded
2019-01-13 | 0.24934 | 0 | 0.11165 | 0.062014 | 0.81365 | 0.73457 | 4.2713 | MAV Exceeded
2019-01-14 | 0.28143 | 0 | 0.25523 | 0.13618 | 0.78188 | 0.70718 | 2.7228 | MAV Exceeded
2019-01-15 | 0.24602 | 0 | 0.29551 | 0.14925 | 0.7965 | 0.71317 | 1.2827
2019-01-16 | 0.23555 | 0 | 0.28262 | 0.14834 | 0.73667 | 0.70004 | 0.86474
2019-01-17 | 0.24056 | 0 | 0.25817 | 0.11619 | 0.36002 | 0.37894 | 0.85811
2019-01-18 | 0.2574 | 0 | 0.27105 | 0.1186 | 0.68574 | 0.73464 | 0.85183
2019-01-19 | 0.17121 | 0 | 0.12246 | 0.055779 | 0.14387 | 0.15104 | 0.85154
2019-01-20 | 0.096307 | 0 | 0.13406 | 0.06009 | 0.074293 | 0.074786 | 0.85741
2019-01-21 | 0.09406 | 0 | 0.12451 | 0.084538 | 0.074769 | 0.074786 | 0.85005
2019-01-22 | 0.09326 | 0 | 0.25296 | 0.092259 | 0.073677 | 0.074823 | 0.8432
2019-01-23 | 0.094853 | 0 | 0.33744 | 0.14204 | 0.30989 | 0.3347 | 0.85301
2019-01-24 | 0.18643 | 0 | 0.39539 | 0.15829 | 0.34921 | 0.38773 | 0.85693
2019-01-25 | 0.10989 | 0.028491 | 0.20614 | 0.076697 | 0.10803 | 0.11476 | 0.86505
2019-01-26 | 0.088337 | 0.094146 | 0.1319 | 0.05152 | 0.074719 | 0.074859 | 0.84458
2019-01-27 | 0.088781 | 0.08724 | 0.14596 | 0.056572 | 0.074769 | 0.074825 | 0.87433
2019-01-28 | 0.087463 | 1.563 | 0.33 | 0.14412 | 0.074786 | 0.074858 | 0.84056 | MAV Exceeded
2019-01-29 | 0.12658 | 0.29437 | 0.19053 | 0.10089 | 0.20439 | 0.21959 | 0.86214
2019-01-30 | 0.089423 | 0.087759 | 0.1146 | 0.065458 | 0.14223 | 0.14916 | 0.85233
2019-01-31 | 0.10013 | 0.091598 | 0.1072 | 0.064967 | 0.082647 | 0.083806 | 0.86515
2019-02-01 | 0.084904 | 0.088058 | 0.11861 | 0.063376 | 0.074786 | 0.074822 | 0.86397
2019-02-02 | 0.085413 | 0.078385 | 0.1269 | 0.065118 | 0.074786 | 0.074786 | 0.8651
2019-02-03 | 0.085195 | 0.080459 | 0.12159 | 0.063203 | 0.074752 | 0.074786 | 0.86609
2019-02-04 | 0.086565 | 0.089276 | 0.11871 | 0.063998 | 0.074786 | 0.074786 | 0.87298
2019-02-05 | 0.085131 | 0.082189 | 0.12042 | 0.065433 | 0.074512 | 0.074825 | 0.8624
2019-02-06 | 0.085325 | 4.8313 | 0.13533 | 0.066537 | 0.074786 | 0.074804 | 0.8664 | MAV Exceeded
2019-02-07 | 0.0849 | 0.24848 | 0.19455 | 0.089306 | 0.069949 | 0.074786 | 0.7526
2019-02-08 | 0.087124 | 0.11846 | 0.19982 | 0.090274 | 0.069082 | 0.074786 | 0.85106
2019-02-09 | 0.08602 | 0.063228 | 0.13803 | 0.064832 | 0.071796 | 0.074786 | 0.85438
2019-02-10 | 0.090241 | 0.063212 | 0.13704 | 0.065802 | 0.074194 | 0.077575 | 0.85458
2019-02-11 | 0.088892 | 0.063133 | 0.13738 | 0.065467 | 0.074786 | 0.074786 | 0.78609
2019-02-12 | 0.084663 | 0.063115 | 0.31078 | 0.17329 | 0.074786 | 0.074786 | 0.51255
2019-02-13 | 0.089136 | 0.070175 | 0.16028 | 0.093616 | 0.074786 | 0.074786 | 0.84187
2019-02-14 | 0.084271 | 0.07967 | 0.22221 | 0.12521 | 0.074786 | 0.074786 | 0.32996
2019-02-15 | 0.083036 | 0.077716 | 0.19369 | 0.1122 | 0.074786 | 0.07482 | 0.33365
2019-02-16 | 0.08116 | 0.077809 | 0.11133 | 0.064341 | 0.074786 | 0.074786 | 0.08565
2019-02-17 | 0.08181 | 0.077519 | 0.10982 | 0.063785 | 0.074786 | 0.074786 | 0.086011
2019-02-18 | 0.082352 | 0.077663 | 0.13016 | 0.076777 | 0.074786 | 0.074786 | 0.30895
2019-02-19 | 0.082669 | 0.075991 | 0.1091 | 0.065402 | 0.074786 | 0.074804 | 0.16688
2019-02-20 | 0.081583 | 0.073811 | 0.11023 | 0.066329 | 0.074786 | 0.074804 | 0.088708
2019-02-21 | 0.081509 | 0.077072 | 0.10947 | 0.06627 | 0.074786 | 0.074786 | 0.088804
2019-02-22 | 0.085151 | 0.080751 | 0.10627 | 0.0652 | 0.074786 | 0.074786 | 0.49607
2019-02-23 | 0.090964 | 0.087271 | 0.10373 | 0.06458 | 0.071799 | 0.07484 | 0.87538
2019-02-24 | 0.088166 | 0.084969 | 0.086594 | 0.052835 | 0.061824 | 0.074786 | 0.43276
2019-02-25 | 0.080508 | 0.077179 | 0.088319 | 0.055128 | 0.050429 | 0.052685 | 0.13996
2019-02-26 | 0.079925 | 0.07617 | 0.077389 | 0.046126 | 0.050366 | 0.050366 | 0.44951
2019-02-27 | 0.085434 | 0.081219 | 0.086952 | 0.050151 | 0.050366 | 0.058349 | 0.86943
2019-02-28 | 0.083989 | 0.079751 | 0.093167 | 0.053469 | 0.050366 | 0.071136 | 0.83654
2019-03-01 | 0.083375 | 0.078742 | 0.095679 | 0.054014 | 0.050366 | 0.066964 | 0.71025
2019-03-02 | 0.079174 | 0.07464 | 0.098874 | 0.055854 | 0.050366 | 0.074634 | 0.10216
2019-03-03 | 0.079405 | 0.074184 | 0.10212 | 0.057241 | 0.050454 | 0.074509 | 0.10539
2019-03-04 | 0.081596 | 0.079928 | 0.10526 | 0.059054 | 0.053168 | 0.074786 | 0.41415
2019-03-05 | 0.085289 | 0.08185 | 0.11049 | 0.061795 | 0.056799 | 0.080461 | 0.32383
2019-03-06 | 0.081949 | 0.078794 | 0.11318 | 0.063252 | 0.45247 | 0.51301 | 0.086767
2019-03-07 | 0.15016 | 0.14173 | 0.26732 | 0.15522 | 0.68708 | 0.72165 | 0.2492
2019-03-08 | 0.15045 | 0.15062 | 0.27334 | 0.14921 | 0.32098 | 0.33686 | 0.14767
2019-03-09 | 0.084109 | 0.079074 | 0.095436 | 0.057254 | 0.13249 | 0.13467 | 0.086522
2019-03-10 | 0.083962 | 0.077181 | 0.092621 | 0.057351 | 0.15242 | 0.15499 | 0.086121
2019-03-11 | 0.09444 | 0.094179 | 0.23613 | 0.15243 | 0.39726 | 0.40421 | 0.18917
2019-03-12 | 0.11752 | 0.11682 | 0.26351 | 0.15191 | 0.59421 | 0.60396 | 0.21833
2019-03-13 | 0.14906 | 0.14013 | 0.37057 | 0.22748 | 0.62236 | 0.61643 | 0.22727
2019-03-14 | 0.14983 | 0.15776 | 0.49761 | 0.34207 | 0.53736 | 0.5608 | 0.087881
2019-03-15 | 0.12156 | 0.11595 | 0.69008 | 0.51118 | 0.41253 | 0.47198 | 0.22149
2019-03-16 | 0.11464 | 0.10998 | 0.64561 | 0.6045 | 0.29306 | 0.33205 | 0.16202
2019-03-17 | 0.11051 | 0.10558 | 0.69405 | 0.64663 | 0.14617 | 0.16164 | 0.08672
2019-03-18 | 0.08204 | 0.082585 | 0.78433 | 0.73178 | 0.10675 | 0.11453 | 0.1331
2019-03-19 | 0.085721 | 0.083335 | 0.69578 | 0.67234 | 0.10461 | 0.10923 | 0.1418
2019-03-20 | 0.085343 | 0.082141 | 0.445 | 0.36838 | 0.11458 | 0.11338 | 0.087632
2019-03-21 | 0.086071 | 0.08207 | 0.059949 | 0.095811 | 0.14109 | 0.14745 | 0.088231
2019-03-22 | 0.09361 | 0.090908 | 0.068277 | 0.061593 | 0.45016 | 0.46772 | 0.15773
2019-03-23 | 0.14103 | 0.14329 | 0.069506 | 0.061367 | 0.55997 | 0.59716 | 0.086203
2019-03-24 | 0.14265 | 0.14025 | 0.068571 | 0.061408 | 0.60637 | 0.64177 | 0.086753
2019-03-25 | 0.17877 | 0.17529 | 0.069693 | 0.063364 | 0.35259 | 0.36682 | 0.089427
2019-03-26 | 0.089122 | 0.086658 | 0.17698 | 0.12205 | 0.10038 | 0.099036 | 0.088545
2019-03-27 | 0.085287 | 0.0824 | 0.1273 | 0.14368 | 0.091739 | 0.096841 | 0.098194
2019-03-28 | 0.084113 | 0.08003 | 0.12606 | 0.13558 | 0.081758 | 0.089684 | 0.10194
2019-03-29 | 0.082848 | 0.079135 | 0.12857 | 0.13717 | 0.075491 | 0.076758 | 0.083549
2019-03-30 | 0.082253 | 0.078005 | 0.050535 | 0.05561 | 0.074786 | 0.074786 | 0.085158
2019-03-31 | 0.081561 | 0.07492 | 0.050504 | 0.057083 | 0.076915 | 0.074786 | 0.084418
2019-04-01 | 0.080017 | 0.075612 | 0.25944 | 0.27797 | 0.077028 | 0.074822 | 0.082937
2019-04-02 | 0.083899 | 0.0803 | 0.34447 | 0.42127 | 0.074786 | 0.074823 | 0.087722
2019-04-03 | 0.082776 | 0.082452 | 0.51716 | 1.4037 | 0.074786 | 0.074786 | 0.091672
2019-04-04 | 0.085978 | 0.080908 | 0.21324 | 0.23538 | 0.074786 | 0.074786 | 0.090793
2019-04-05 | 0.085042 | 0.082179 | 0.45228 | 0.35154 | 0.074786 | 0.074786 | 0.087828
2019-04-06 | 0.087017 | 0.083256 | 0.068023 | 0.064821 | 0.085753 | 0.086356 | 0.085357
2019-04-07 | 0.092647 | 0.087327 | 0.042881 | 0.048538 | 0.12999 | 0.14415 | 0.090689
2019-04-07 23:00 | 0.086667 | 0.081626 | 0.37502 | 0.40227 | 0.10988 | 0.11854 | 0.10648
2019-04-08 23:00 | 0.079475 | 0.075762 | 0.51917 | 0.46086 | 0.072555 | 0.070902 | 0.085134
2019-04-09 23:00 | 0.081666 | 0.07608 | 0.42478 | 0.39748 | 0.14234 | 0.1452 | 0.086206
2019-04-10 23:00 | 0.089521 | 0.085581 | 0.40067 | 0.43799 | 0.085792 | 0.083688 | 0.08821
2019-04-11 23:00 | 0.088358 | 0.083997 | 0.38745 | 0.65417 | 0.11379 | 0.11122 | 0.087782
2019-04-12 23:00 | 0.086303 | 0.081708 | 0.52108 | 0.43871 | 0.072982 | 0.069501 | 0.085922
2019-04-13 23:00 | 0.078397 | 0.072696 | 0.07488 | 0.06959 | 0.071535 | 0.063693 | 0.084463
2019-04-14 23:00 | 0.068312 | 0.07856 | 0.31988 | 0.32302 | 0.16367 | 0.16869 | 0.099228
2019-04-15 23:00 | 0.085703 | 0.098723 | 0.34682 | 0.3408 | 0.32361 | 0.29793 | 0.087302
2019-04-16 23:00 | 0.13623 | 0.13203 | 0.31472 | 0.30387 | 0.30494 | 0.2691 | 0.096873
2019-04-17 23:00 | 0.11398 | 0.11011 | 0.26168 | 0.28027 | 0.16516 | 0.13964 | 0.085237
2019-04-18 23:00 | 0.085219 | 0.080164 | 0.22111 | 0.20962 | 0.095025 | 0.074786 | 0.086194
2019-04-19 23:00 | 0.084789 | 0.078628 | 0.14372 | 0.11222 | 0.099705 | 0.074786 | 0.087568
2019-04-20 23:00 | 0.086064 | 0.080328 | 0.13735 | 0.10173 | 0.10073 | 0.075039 | 0.087644
2019-04-21 23:00 | 0.085164 | 0.079837 | 0.10908 | 0.08156 | 0.090908 | 0.074786 | 0.087486
2019-04-22 23:00 | 0.086845 | 0.081092 | 0.19422 | 0.13549 | 0.17315 | 0.13889 | 0.10306
2019-04-23 23:00 | 0.094857 | 0.090686 | 0.2906 | 0.22027 | 0.16722 | 0.13253 | 0.088335
2019-04-24 23:00 | 0.091138 | 0.084861 | 0.18602 | 0.11829 | 0.10073 | 0.074786 | 0.086257
2019-04-25 23:00 | 0.086491 | 0.081355 | 0.19607 | 0.11056 | 0.1643 | 0.13228 | 0.088169
2019-04-26 23:00 | 0.092882 | 0.0886 | 0.10398 | 0.055243 | 0.10073 | 0.076498 | 0.090084
2019-04-27 23:00 | 0.087893 | 0.085914 | 0.13345 | 0.056345 | 0.10392 | 0.08543 | 0.091192
2019-04-28 23:00 | 0.092918 | 0.086813 | 0.31266 | 0.12766 | 0.18123 | 0.15613 | 0.090009
2019-04-29 23:00 | 0.090544 | 0.08233 | 0.46488 | 0.19786 | 0.076398 | 0.074672 | 0.098883
2019-04-30 23:00 | 0.092268 | 0.085846 | 0.22376 | 0.080116 | 0.20466 | 0.20667 | 0.084074
2019-05-01 23:00 | 0.11178 | 0.10739 | 0.14512 | 0.055644 | 0.2326 | 0.23104 | 0.084209
2019-05-02 23:00 | 0.11723 | 0.11476 | 0.092788 | 0.055908 | 0.34508 | 0.35052 | 0.084694
2019-05-03 23:00 | 0.13908 | 0.1347 | 0.058524 | 0.050208 | 0.39975 | 0.40689 | 0.084524
2019-05-04 23:00 | 0.13576 | 0.12578 | 0.099228 | 0.053286 | 0.43003 | 0.43768 | 0.085949
2019-05-05 23:00 | 0.15831 | 0.12666 | 0.13344 | 0.062394 | 0.33188 | 0.33739 | 0.086839
2019-05-06 23:00 | 0.18297 | 0.17905 | 0.18833 | 0.057738 | 0.15439 | 0.15322 | 0.13265
2019-05-07 23:00 | 0.38751 | 0.38539 | 0.21517 | 0.057169 | 0.079171 | 0.076683 | 0.088529
2019-05-08 23:00 | 0.29074 | 0.28282 | 0.28496 | 0.058134 | 0.10484 | 0.10128 | 0.089486
2019-05-09 23:00 | 0.086611 | 0.080079 | 0.33552 | 0.060312 | 0.083159 | 0.080283 | 0.089556
2019-05-10 23:00 | 0.086666 | 0.078646 | 0.35967 | 0.061655 | 0.077519 | 0.074876 | 0.092662
2019-05-11 23:00 | 0.08667 | 0.078127 | 0.42452 | 0.055116 | 0.077176 | 0.074823 | 0.092447
2019-05-12 23:00 | 0.086695 | 0.078284 | 0.50538 | 0.054795 | 0.074948 | 0.074786 | 0.095339
2019-05-13 23:00 | 0.086933 | 0.080488 | 0.57528 | 0.054349 | 0.13429 | 0.13586 | 0.091435
2019-05-14 23:00 | 0.086736 | 0.086843 | 0.56247 | 0.049859 | 0.11761 | 0.11828 | 0.15045
2019-05-15 23:00 | 0.08671 | 0.079864 | 0.73159 | 0.050011 | 0.10487 | 0.10326 | 0.12489
2019-05-16 23:00 | 0.087025 | 0.079214 | 0.82173 | 0.05053 | 0.075927 | 0.074786 | 0.16981
2019-05-17 23:00 | 0.087104 | 0.077813 | 0.9679 | 0.051162 | 0.075255 | 0.074786 | 0.083201
2019-05-18 23:00 | 0.086948 | 0.078748 | 1.1578 | 0.055297 | 0.075981 | 0.074786 | 0.083469
2019-05-19 23:00 | 0.086971 | 0.076454 | 1.3923 | 0.055753 | 0.075189 | 0.074786 | 0.11257
2019-05-20 23:00 | 0.087049 | 0.074912 | 1.3566 | 0.056123 | 0.074786 | 0.074786 | 0.17232
2019-05-21 23:00 | 0.086982 | 0.075123 | 1.5651 | 0.057433 | 0.074786 | 0.074786 | 0.16398 | MAV Exceeded
2019-05-22 23:00 | 0.087024 | 0.073447 | 1.4425 | 0.058157 | 0.074786 | 0.074786 | 0.078904
2019-05-23 23:00 | 0.087001 | 0.072468 | 1.4904 | 0.05831 | 0.074786 | 0.074786 | 0.09057
2019-05-24 23:00 | 0.086944 | 0.073761 | 1.5606 | 0.058943 | 0.074786 | 0.074786 | 0.078866 | MAV Exceeded
2019-05-25 23:00 | 0.086812 | 0.073463 | 1.6909 | 0.060097 | 0.074786 | 0.074786 | 0.080008 | MAV Exceeded
2019-05-26 23:00 | 0.086676 | 0.073899 | 1.7556 | 0.062929 | 0.074786 | 0.074786 | 0.081137 | MAV Exceeded
2019-05-27 23:00 | 0.086673 | 0.076993 | 1.82 | 0.063854 | 0.074786 | 0.07644 | 0.13416 | MAV Exceeded
2019-05-28 23:00 | 0.086673 | 0.08021 | 1.6727 | 0.064412 | 0.077151 | 0.081457 | 0.084827 | MAV Exceeded
2019-05-29 23:00 | 0.086651 | 0.080631 | 1.5803 | 0.061696 | 0.07531 | 0.078575 | 0.085749 | MAV Exceeded
2019-05-30 23:00 | 0.08667 | 0.077752 | 1.6597 | 0.058824 | 0.074786 | 0.074786 | 0.16037 | MAV Exceeded
2019-05-31 23:00 | 0.087012 | 0.077921 | 1.8049 | 0.057763 | 0.071521 | 0.074786 | 0.092312 | MAV Exceeded
2019-06-01 23:00 | 0.087088 | 0.082095 | 2.1263 | 0.055669 | 0.072213 | 0.074364 | 0.09606 | MAV Exceeded
2019-06-02 23:00 | 0.087178 | 0.078378 | 2.2765 | 0.054054 | 0.055332 | 0.059522 | 0.098 | MAV Exceeded
2019-06-03 23:00 | 0.087057 | 0.082213 | 2.5082 | 0.047077 | 0.056802 | 0.064711 | 0.15308 | MAV Exceeded
2019-06-04 23:00 | 0.087054 | 0.080921 | 3.0447 | 0.049433 | 0.066846 | 0.074562 | 0.23338 | MAV Exceeded
2019-06-05 23:00 | 0.087267 | 0.080358 | 3.2368 | 0.052309 | 0.054522 | 0.061296 | 0.23864 | MAV Exceeded
2019-06-06 23:00 | 0.087072 | 0.078356 | 3.0739 | 0.048733 | 0.054832 | 0.065524 | 0.16517 | MAV Exceeded
2019-06-07 23:00 | 0.087319 | 0.079381 | 3.1913 | 0.046965 | 0.056301 | 0.067719 | 0.086143 | MAV Exceeded
2019-06-08 23:00 | 0.087351 | 0.079908 | 2.835 | 0.048594 | 0.057083 | 0.074753 | 0.087201 | MAV Exceeded
2019-06-09 23:00 | 0.087072 | 0.08121 | 2.1376 | 0.073735 | 0.061128 | 0.074786 | 0.20153 | MAV Exceeded
2019-06-10 23:00 | 0.086995 | 0.1275 | 2.6544 | 0.058149 | 0.068786 | 0.074786 | 0.19279 | MAV Exceeded
2019-06-11 23:00 | 0.087043 | 0.0804 | 2.8887 | 0.056607 | 0.069949 | 0.074786 | 0.18758 | MAV Exceeded
2019-06-12 23:00 | 0.087025 | 0.086938 | 2.9067 | 0.054336 | 0.070212 | 0.074786 | 0.25594 | MAV Exceeded
2019-06-13 23:00 | 0.086945 | 0.08702 | 3.0372 | 0.086574 | 0.078874 | 0.091386 | 0.086471 | MAV Exceeded
2019-06-14 23:00 | 0.08705 | 0.079231 | 2.8844 | 0.052724 | 0.0544 | 0.067281 | 0.086858 | MAV Exceeded
2019-06-15 23:00 | 0.087052 | 0.080763 | 3.2559 | 0.051289 | 0.062664 | 0.073381 | 0.08758 | MAV Exceeded
2019-06-16 23:00 | 0.087178 | 0.084261 | 3.6013 | 0.051959 | 0.059462 | 0.073596 | 0.11057 | MAV Exceeded
2019-06-17 23:00 | 0.08731 | 0.10279 | 3.5236 | 0.053676 | 0.06294 | 0.074786 | 0.26572 | MAV Exceeded
2019-06-18 23:00 | 0.087429 | 0.082444 | 3.5041 | 0.054417 | 0.060042 | 0.074396 | 0.26757 | MAV Exceeded
2019-06-19 23:00 | 0.087448 | 0.083724 | 3.6629 | 0.055986 | 0.061092 | 0.072352 | 0.086188 | MAV Exceeded
2019-06-20 23:00 | 0.087183 | 0.11071 | 1.7076 | 0.056909 | 0.063299 | 0.074531 | 0.087586 | MAV Exceeded
2019-06-21 23:00 | 0.087043 | 0.083011 | 0 | 0.0584 | 0.07042 | 0.13733 | 0.086324
2019-06-22 23:00 | 0.087057 | 0.08316 | 0 | 0.057774 | 0.070958 | 0.15157 | 0.088164
2019-06-23 23:00 | 0.058167 | 0.089266 | 0.042684 | 0.070146 | 0.069128 | 0.12135 | 0.090817
2019-06-24 23:00 | 0 | 0.099551 | 0.065234 | 0.084197 | 0.078025 | 0.074919 | 0.11385
2019-06-25 23:00 | 0 | 0.085673 | 0.080487 | 0.10518 | 0.096785 | 0.08312 | 0.080815
2019-06-26 23:00 | 0.045075 | 0.094587 | 0.06944 | 0.082973 | 0.095197 | 0.074126 | 0.22436
2019-06-27 23:00 | 0.086205 | 0.086424 | 0.059147 | 0.076545 | 0.10048 | 0.068903 | 0.16828
2019-06-28 23:00 | 0.084817 | 0.086619 | 0.044021 | 0.055826 | 0.10073 | 0.074809 | 0.086513
2019-06-29 23:00 | 0.086133 | 0.087559 | 0.0484 | 0.059368 | 0.10073 | 0.074771 | 0.090209
2019-06-30 23:00 | 0.084977 | 0.085164 | 0.056955 | 0.068924 | 0.1008 | 0.075177 | 0.181

## 19-20
Date Stamp | .Gear Island 1050 Fluoride | .Gear Island 1050 Fluoride Analyser #2 | .Te Marua PS Fluoride Residual | .Te Marua TP Fluoride Residual | .Wainui Fluoride Building Fluoride Residual Stream 1 | .Wainui Fluoride Building Fluoride Residual Stream 2 | .Waterloo Naenae Fluoride Residual
2019-07-01 23:00 | 0.079306 | 0.07692 | 0.098857 | 0.11853 | 0.078196 | 0.0609 | 0.20192
2019-07-02 23:00 | 0.080543 | 0.080089 | 0.087901 | 0.10105 | 0.05085 | 0.04851 | 0.19549
2019-07-03 23:00 | 0.081689 | 0.085467 | 0.0596 | 0.067845 | 0.051415 | 0.048284 | 0.16676
2019-07-04 23:00 | 0.087683 | 0.087404 | 0.12989 | 0.13639 | 0.069693 | 0.058563 | 0.21789
2019-07-05 23:00 | 0.087004 | 0.090347 | 0.047629 | 0.05682 | 0.078785 | 0.073962 | 0.090279
2019-07-06 23:00 | 0.086195 | 0.088463 | 0.046496 | 0.054879 | 0.094698 | 0.079627 | 0.090223 |  | Fluoride not dosed
2019-07-07 23:00 | 0.088443 | 0.090681 | 0.068256 | 0.075044 | 0.078969 | 0.071901 | 0.31535 |  | fluoride dosed but outside recommended range
2019-07-08 23:00 | 0.083972 | 0.092147 | 0.11382 | 0.12802 | 0.050366 | 0.051045 | 0.27826 |  | Fluoride dosed but within recommended range
2019-07-09 23:00 | 0.082933 | 0.085029 | 0.12863 | 0.14556 | 0.050366 | 0.053101 | 0.18147
2019-07-10 23:00 | 0.092597 | 0.077625 | 0.047165 | 0.054037 | 0.055295 | 0.05451 | 0.089037 | Assumptions: |  | 1. Values less than 0.1 indicates that fluoride is not being dosed
2019-07-11 23:00 | 0.08028 | 0.083509 | 0.10418 | 0.11621 | 0.053895 | 0.056909 | 0.089998 |  |  | 2. MAV exceedences are due to the default value that the analyser goes to when fluoride dosing is ceased
2019-07-12 23:00 | 0.080376 | 0.084679 | 0.043762 | 0.050761 | 0.057123 | 0.058521 | 0.092753 |  |  | 3. The Gear Island sampling point is downstream of the plant and can contain a residual from the Wainuiomata WTP
2019-07-13 23:00 | 0.079769 | 0.084997 | 0.04212 | 0.049517 | 0.058269 | 0.06783 | 0.090566
2019-07-14 23:00 | 0.079947 | 0.081239 | 0.089787 | 0.096459 | 0.050366 | 0.052462 | 0.096031
2019-07-15 23:00 | 0.07994 | 0.083527 | 0.12425 | 0.13122 | 0.05091 | 0.063342 | 0.10356
2019-07-16 23:00 | 0.079897 | 0.079157 | 0.26786 | 0.29177 | 0.050366 | 0.055238 | 0.093779
2019-07-17 23:00 | 0.080084 | 0.076723 | 0.28762 | 0.2899 | 0.050366 | 0.059722 | 0.095568
2019-07-18 23:00 | 0.079991 | 0.080337 | 0.17972 | 0.16499 | 0.05291 | 0.072424 | 0.09545
2019-07-19 23:00 | 0.079917 | 0.083287 | 0.041743 | 0.048562 | 0.058081 | 0.074013 | 0.099382
2019-07-20 23:00 | 0.080125 | 0.082005 | 0.040754 | 0.047669 | 0.053408 | 0.070827 | 0.10225
2019-07-21 23:00 | 0.080043 | 0.081911 | 0.23354 | 0.22502 | 0.050366 | 0.067852 | 0.10117
2019-07-22 23:00 | 0.080175 | 0.090584 | 0.084339 | 0.085457 | 0.054093 | 0.072401 | 0.091288
2019-07-23 23:00 | 0.08012 | 0.081917 | 0.050007 | 0.053006 | 0.20542 | 0.23855 | 0.092614
2019-07-24 23:00 | 0.080069 | 0.15674 | 0.051888 | 0.054127 | 0.35423 | 0.38787 | 0.094094
2019-07-25 23:00 | 0.080148 | 0.14115 | 0.053305 | 0.054916 | 0.17232 | 0.19716 | 0.093651
2019-07-26 23:00 | 0.080122 | 0.10844 | 0.05492 | 0.056396 | 0.24678 | 0.30461 | 0.094437
2019-07-27 23:00 | 0.079862 | 0.27251 | 0.059077 | 0.058947 | 0.35811 | 0.42856 | 0.099038
2019-07-28 23:00 | 0.079953 | 0.089505 | 0.060875 | 0.059596 | 0.068067 | 0.090614 | 0.097927
2019-07-29 23:00 | 0.080015 | 0.084766 | 0.060455 | 0.059604 | 0.081342 | 0.11909 | 0.096957
2019-07-30 23:00 | 0.080125 | 0.095068 | 0.061477 | 0.06009 | 0.11543 | 0.16549 | 0.099248
2019-07-31 23:00 | 0.080184 | 0.082955 | 0.060867 | 0.059738 | 0.14752 | 0.23674 | 0.098689
2019-08-01 23:00 | 0.080237 | 0.18762 | 0.049979 | 0.059895 | 0.45314 | 0.62877 | 0.099555
2019-08-02 23:00 | 0.080144 | 0.20722 | 0.049023 | 0.059854 | 0.31207 | 0.37545 | 0.10118
2019-08-03 23:00 | 0.080044 | 0.13528 | 0.050356 | 0.059687 | 0.14241 | 0.23694 | 0.10322
2019-08-04 23:00 | 0.080193 | 0.086605 | 0.04986 | 0.059914 | 0.083684 | 0.1824 | 0.10742
2019-08-05 23:00 | 0.080304 | 0.089737 | 0.048962 | 0.056741 | 0.085321 | 0.14819 | 0.11122
2019-08-06 23:00 | 0.080202 | 0.090943 | 0.054063 | 0.055506 | 0.20852 | 0.047212 | 0.1163
2019-08-07 23:00 | 0.080047 | 0.16094 | 0.058052 | 0.057844 | 0.20529 | 0.046886 | 0.11681
2019-08-08 23:00 | 0.079854 | 0.099766 | 0.057597 | 0.056567 | 0.25461 | 0.077303 | 0.12074
2019-08-09 23:00 | 0.080028 | 0.21436 | 0.055318 | 0.054254 | 0.74595 | 0.30139 | 0.12909
2019-08-10 23:00 | 0.079884 | 0.22504 | 0.054915 | 0.053604 | 0.60098 | 0.2975 | 0.11972
2019-08-11 23:00 | 0.07998 | 0.26512 | 0.056669 | 0.054389 | 0.78343 | 0.49025 | 0.12876
2019-08-12 23:00 | 0.080102 | 0.14485 | 0.05688 | 0.05389 | 0.41227 | 0.27527 | 0.13273
2019-08-13 23:00 | 0.080176 | 0.14965 | 0.051241 | 0.049826 | 0.14395 | 0.05712 | 0.12029
2019-08-14 23:00 | 0.080189 | 0.24006 | 0.050538 | 0.04939 | 0.50215 | 0.54085 | 0.092129
2019-08-15 23:00 | 0.080148 | 0.5866 | 0.054159 | 0.051807 | 0.72276 | 0.78142 | 0.092521
2019-08-16 23:00 | 0.080123 | 0.36233 | 0.057877 | 0.054173 | 0.31022 | 0.4288 | 0.093827
2019-08-17 23:00 | 0.080192 | 0.46826 | 0.059572 | 0.055497 | 0.32574 | 0.29237 | 0.094876
2019-08-18 23:00 | 0.080417 | 0.40776 | 0.056833 | 0.053458 | 0.07892 | 0.057946 | 0.12232
2019-08-19 23:00 | 0.080355 | 0.45707 | 0.052992 | 0.051132 | 0.063197 | 0.073929 | 0.080718
2019-08-20 23:00 | 0.080177 | 0.44582 | 0.055756 | 0.052901 | 0.064647 | 0.071935 | 0.10126
2019-08-21 23:00 | 0.080052 | 0.64597 | 0.060613 | 0.055307 | 0.82886 | 0.064973 | 0.13159
2019-08-22 23:00 | 0.080144 | 0.49711 | 0.064182 | 0.057 | 0.074786 | 0.06226 | 0.10509
2019-08-23 23:00 | 0.080152 | 0.52876 | 0.058164 | 0.053076 | 0.070119 | 0.067897 | 0.10637
2019-08-24 23:00 | 0.080133 | 0.56011 | 0.052223 | 0.049173 | 0.065588 | 0.077221 | 0.095952
2019-08-25 23:00 | 0.079852 | 0.57208 | 0.055494 | 0.051132 | 0.068183 | 0.089322 | 0.12217
2019-08-26 23:00 | 0.079906 | 0.46128 | 0.063983 | 0.056556 | 0.06016 | 0.072739 | 0.10019
2019-08-27 23:00 | 0.080121 | 0.463 | 0.062349 | 0.055661 | 0.057947 | 0.073212 | 0.0967
2019-08-28 23:00 | 0.080026 | 0.61019 | 0.065667 | 0.056039 | 0.057921 | 0.084257 | 0.096625
2019-08-29 23:00 | 0.079959 | 0.47049 | 0.067802 | 0.057112 | 0.062845 | 0.073226 | 0.098682
2019-08-30 23:00 | 0.08004 | 0.44819 | 0.068453 | 0.057883 | 0.065512 | 0.067186 | 0.10355
2019-08-31 23:00 | 0.080056 | 0.46977 | 0.069127 | 0.058167 | 0.066977 | 0.07874 | 0.10707
2019-09-01 23:00 | 0.079919 | 0.35728 | 0.36144 | 0.28314 | 0.072232 | 0.10241 | 0.11374
2019-09-02 23:00 | 0.079961 | 0.38772 | 0.73281 | 0.51718 | 0.068617 | 0.11762 | 0.21035
2019-09-03 23:00 | 0.079833 | 0.45596 | 0.92153 | 0.68373 | 0.07116 | 0.16107 | 0.11276
2019-09-04 23:00 | 0.23223 | 0.53043 | 0.80304 | 0.65637 | 0.07695 | 0.34157 | 0.53563
2019-09-05 23:00 | 0.50573 | 0.49786 | 0.80704 | 0.63926 | 0.081462 | 0.38826 | 0.15833
2019-09-06 23:00 | 0.77933 | 0.78282 | 0.47767 | 0.36112 | 0.054731 | 0.35174 | 0.10116
2019-09-07 23:00 | 0.69882 | 0.69828 | 0.093127 | 0.064842 | 0.059753 | 0.39335 | 0.09683
2019-09-08 23:00 | 0.51095 | 0.51529 | 0.2569 | 0.18956 | 0.064253 | 0.39452 | 0.1096
2019-09-09 23:00 | 0.084328 | 0.081173 | 0.3121 | 0.28457 | 0.054952 | 0.51998 | 0.10599
2019-09-10 23:00 | 0.65977 | 0.68969 | 0.25218 | 0.25435 | 0.051197 | 0.41423 | 0.26642
2019-09-11 23:00 | 0.39392 | 0.4012 | 0.31186 | 0.26771 | 0.054455 | 0.61376 | 0.22391
2019-09-12 23:00 | 0.57425 | 0.57876 | 0.81935 | 0.62248 | 0.064527 | 0.74808 | 0.22866
2019-09-13 23:00 | 0.6988 | 0.68063 | 0.25146 | 0.16318 | 0.066037 | 0.80257 | 0.096487
2019-09-14 23:00 | 0.74548 | 0.75553 | 0.23746 | 0.20906 | 0.055426 | 0.72933 | 0.099232
2019-09-15 23:00 | 0.78023 | 0.79324 | 0.62519 | 0.4178 | 0.050366 | 0.80752 | 0.13305
2019-09-16 23:00 | 0.74293 | 0.75676 | 0.39662 | 0.35041 | 0.05647 | 0.96246 | 0.10812
2019-09-17 23:00 | 0.61361 | 0.60452 | 0.30645 | 0.21201 | 0.051533 | 0.56669 | 0.10149
2019-09-18 23:00 | 0.56363 | 0.5538 | 0.43988 | 0.3861 | 0.055526 | 0.63097 | 0.10366
2019-09-19 23:00 | 0.57177 | 0.61622 | 0.75885 | 0.59291 | 0.052412 | 0.42324 | 0.16646
2019-09-20 23:00 | 0.61427 | 0.70907 | 0.77576 | 0.60767 | 0.050366 | 0.050366 | 0.14126
2019-09-21 23:00 | 0.6117 | 0.709 | 0.3497 | 0.24626 | 0.050366 | 0.050366 | 0.12663
2019-09-22 23:00 | 0.55109 | 0.57622 | 0.33323 | 0.30801 | 0.050366 | 0.050366 | 0.22195
2019-09-23 23:00 | 0.75991 | 0.76493 | 0.67119 | 0.53959 | 0.050482 | 0.052859 | 0.21647
2019-09-24 23:00 | 0.88201 | 0.8938 | 0.48278 | 0.33793 | 0.072347 | 0.081687 | 0.17292
2019-09-25 23:00 | 0.76601 | 0.73457 | 0.36267 | 0.32103 | 0.07187 | 0.075088 | 0.40806
2019-09-26 23:00 | 0.63072 | 0.63994 | 0.7204 | 0.60265 | 0.048891 | 0.050366 | 0.2247
2019-09-27 23:00 | 0.63063 | 0.64215 | 0.72118 | 0.61797 | 0.050383 | 0.05222 | 0.091198
2019-09-28 23:00 | 0.62287 | 0.62729 | 0.69623 | 0.59712 | 0.051261 | 0.05578 | 0.10357
2019-09-30 | 0.60659 | 0.63489 | 0.70523 | 0.61252 | 0.059708 | 0.052546 | 0.10845
2019-10-01 | 0.54836 | 0.55589 | 0.3487 | 0.28936 | 0.055338 | 0.050274 | 0.10402
2019-10-02 | 0.64526 | 0.68536 | 0.70312 | 0.59906 | 0.050366 | 0.048604 | 0.12634
2019-10-03 | 0.8671 | 0.90081 | 0.71902 | 0.59535 | 0.050366 | 0.050366 | 0.099615
2019-10-04 | 0.87099 | 0.87803 | 0.71639 | 0.59572 | 0.05536 | 0.055208 | 0.10086
2019-10-05 | 0.8716 | 0.89036 | 0.42838 | 0.3317 | 0.058664 | 0.053603 | 0.10282
2019-10-06 | 0.85842 | 0.87227 | 0.1912 | 0.19124 | 0.074186 | 0.071663 | 0.16414
2019-10-07 | 0.84239 | 0.82138 | 0.31185 | 0.21909 | 0.074823 | 0.074786 | 0.1492
2019-10-08 | 0.87224 | 0.89229 | 0.12275 | 0.1163 | 0.07554 | 0.07493 | 0.10911
2019-10-09 | 0.4737 | 0.4601 | 0.098347 | 0.090755 | 0.08724 | 0.077526 | 0.32268
2019-10-10 | 0.396 | 0.41449 | 0.1269 | 0.11224 | 0.096968 | 0.093119 | 0.12645
2019-10-11 | 0.86859 | 0.90115 | 0.094276 | 0.086378 | 0.093708 | 0.082593 | 2.7527
2019-10-12 | 0.86654 | 0.8885 | 0.058133 | 0.055041 | 0.052624 | 0.058247 | 5
2019-10-13 | 0.86387 | 0.86073 | 0.053857 | 0.051705 | 0.057541 | 0.059103 | 5
2019-10-14 | 0.81095 | 0.8063 | 0.074699 | 0.060138 | 0.063828 | 0.062013 | 5
2019-10-15 | 0.56693 | 0.58676 | 0.098179 | 0.084009 | 0.058265 | 0.055302 | 5
2019-10-16 | 0.59537 | 0.60117 | 0.076484 | 0.074652 | 0.061783 | 0.05771 | 5
2019-10-17 | 0.86391 | 0.88149 | 0.060556 | 0.055933 | 0.059316 | 0.058513 | 5
2019-10-18 | 0.79891 | 0.80802 | 0.05598 | 0.052652 | 0.060278 | 0.054513 | 5
2019-10-19 | 0.81032 | 0.8107 | 0.058705 | 0.055246 | 0.059901 | 0.056031 | 5
2019-10-20 | 0.81491 | 0.86205 | 0.058785 | 0.054234 | 0.051219 | 0.050383 | 5
2019-10-21 | 0.79807 | 0.78196 | 0.053756 | 0.049086 | 0.050875 | 0.050366 | 5
2019-10-22 | 0.78933 | 0.79667 | 0.052241 | 0.050613 | 0.050383 | 0.050366 | 5
2019-10-23 | 0.80314 | 0.81711 | 0.037055 | 0.054151 | 0.050725 | 0.050366 | 4.06
2019-10-24 | 0.74883 | 0.93101 | 0.037024 | 0.053468 | 0.051558 | 0.050366 | 3.5719
2019-10-25 | 0.77241 | 0.44122 | 0.033889 | 0.048088 | 0.053088 | 0.050366 | 1.877
2019-10-26 | 0.70335 | 0.72015 | 0.035584 | 0.049968 | 0.052297 | 0.050366 | 5
2019-10-27 | 0.8214 | 0.83605 | 0.040481 | 0.053644 | 0.053378 | 0.050366 | 5
2019-10-28 | 0.77882 | 0.90903 | 0.043146 | 0.054421 | 0.057617 | 0.051583 | 5
2019-10-29 | 0.79556 | 0.81855 | 0.043296 | 0.053722 | 0.052982 | 0.050366 | 5
2019-10-30 | 0.80584 | 0.82706 | 0.19588 | 0.22975 | 0.041964 | 0.035437 | 5
2019-10-31 | 0.73932 | 0.76889 | 0.56566 | 0.55047 | 0.033236 | 0.02442 | 3.8572
2019-11-01 | 0.60921 | 0.61195 | 0.5076 | 0.51565 | 0.033096 | 0.02442 | 0.97327
2019-11-02 | 0.57968 | 0.58195 | 0.71851 | 0.69969 | 0.032894 | 0.02442 | 0.86222
2019-11-03 | 0.60059 | 0.60698 | 0.7257 | 0.69793 | 0.034307 | 0.02442 | 0.76654
2019-11-04 | 0.67591 | 0.68737 | 0.55899 | 0.52077 | 0.035217 | 0.02442 | 0.52506
2019-11-05 | 0.68042 | 0.6868 | 0.47269 | 0.44751 | 0.040481 | 0.029365 | 0.84788
2019-11-06 | 0.71909 | 0.72435 | 0.42467 | 0.43978 | 1.1523 | 4.2524 | 0.80013
2019-11-07 | 0.60337 | 0.60098 | 0.64892 | 0.62837 | 3.5584 | 5 | 0.77303 | MAV exceeded
2019-11-08 | 0.64144 | 0.65004 | 0.31165 | 0.28971 | 4.966 | 5 | 0.7274 | MAV exceeded
2019-11-09 | 0.61049 | 0.61303 | 0.56634 | 0.6037 | 4.9395 | 5 | 0.80175 | MAV exceeded
2019-11-10 | 0.66512 | 0.68439 | 0.33439 | 0.33963 | 4.9962 | 5 | 0.81437 | MAV exceeded
2019-11-11 | 0.84728 | 0.86461 | 0.60019 | 0.58372 | 4.9997 | 5 | 0.59652 | MAV exceeded
2019-11-12 | 0.85733 | 0.87589 | 0.48123 | 0.44063 | 3.0982 | 2.8439 | 0.75201 | MAV exceeded
2019-11-13 | 0.84189 | 0.87296 | 0.36299 | 0.34124 | 0.87969 | 5.0768e-05 | 0.5368
2019-11-14 | 0.77615 | 0.80015 | 0.48895 | 0.44907 | 3.2463 | 0.007163 | 0.64341 | MAV exceeded
2019-11-15 | 0.57203 | 0.58258 | 0.49401 | 0.4498 | 0.044086 | 0.02442 | 0.52115
2019-11-16 | 0.51798 | 0.52181 | 0.067157 | 0.065872 | 0.047807 | 0.02442 | 0.68093
2019-11-17 | 0.51197 | 0.49875 | 0.206 | 0.18506 | 0.047673 | 0.02442 | 0.087251
2019-11-18 | 0.53606 | 0.92872 | 0.32514 | 0.37462 | 0.04671 | 0.02442 | 0.41
2019-11-19 | 0.57914 | 0.5361 | 0.54245 | 0.50599 | 0.041736 | 0.02442 | 0.47737
2019-11-20 | 0.65481 | 0.64152 | 0.59465 | 0.55843 | 0.044776 | 0.02442 | 0.649
2019-11-21 | 0.54373 | 0.53283 | 0.48141 | 0.51799 | 0.045276 | 0.02442 | 0.48732
2019-11-22 | 0.55926 | 0.54866 | 0.57585 | 0.54144 | 0.046644 | 0.02442 | 0.084434
2019-11-23 | 0.53371 | 0.52654 | 0.33985 | 0.27579 | 0.050366 | 0.02451 | 0.086331
2019-11-24 | 0.54021 | 0.5312 | 0.066298 | 0.066518 | 0.050366 | 0.025393 | 0.088318
2019-11-25 | 0.55787 | 0.55176 | 0.39499 | 0.39518 | 0.050366 | 0.026925 | 0.26802
2019-11-26 | 0.51878 | 0.49724 | 0.72549 | 0.6428 | 0.050366 | 0.02442 | 0.24707
2019-11-27 | 1.0681 | 0.38459 | 0.72883 | 0.63703 | 0.050366 | 0.02442 | 0.11898
2019-11-28 | 1.2265 | 0.53596 | 0.74992 | 0.6608 | 0.050169 | 0.02442 | 0.50608
2019-11-29 | 0.54811 | 0.54602 | 0.6042 | 0.53454 | 0.050187 | 0.037672 | 0.64438
2019-11-30 | 0.58994 | 0.5846 | 0.72623 | 0.64229 | 0.050366 | 0.050258 | 0.1901
2019-12-01 | 0.6125 | 0.60812 | 0.61176 | 0.52042 | 0.050366 | 0.05033 | 0.089543
2019-12-02 | 0.57251 | 0.57051 | 0.75234 | 0.6837 | 0.050186 | 0.050186 | 0.18682
2019-12-03 | 0.63249 | 0.63079 | 0.75946 | 0.66821 | 0.046816 | 0.03726 | 0.26906
2019-12-04 | 0.67928 | 0.85967 | 0.78771 | 0.7189 | 0.033515 | 0.025987 | 0.58812
2019-12-05 | 0.69439 | 0.67796 | 0.72762 | 0.60677 | 0.041462 | 0.031574 | 0.77501
2019-12-06 | 0.74467 | 0.67519 | 0.68528 | 0.57971 | 0.049336 | 0.041346 | 0.088899
2019-12-07 | 0.74279 | 0.6875 | 0.57956 | 0.5075 | 0.046867 | 0.043159 | 0.08899
2019-12-08 | 0.87876 | 0.65435 | 0.78453 | 0.67725 | 0.048783 | 0.049662 | 0.086085
2019-12-09 | 0.87895 | 0.49704 | 0.7662 | 0.65032 | 0.050366 | 0.050312 | 0.13121
2019-12-10 | 0.87892 | 0.74214 | 0.54373 | 0.42427 | 0.048126 | 0.046259 | 0.1967
2019-12-11 | 0.87884 | 0.49211 | 0.26062 | 0.28956 | 0.041789 | 0.038287 | 0.24497
2019-12-12 | 0.87862 | 0.43106 | 0.13996 | 0.14242 | 0.057435 | 0.045719 | 0.29907
2019-12-13 | 0.87876 | 0.47653 | 0.35485 | 0.39139 | 0.050348 | 0.050366 | 0.50044
2019-12-14 | 0.87872 | 0.44505 | 0.67771 | 0.68348 | 0.048601 | 0.050366 | 0.65694
2019-12-15 | 0.87884 | 0.5422 | 0.48968 | 0.46265 | 0.048298 | 0.050366 | 0.54217
2019-12-16 | 0.87879 | 0.45689 | 0.2272 | 0.22369 | 0.050638 | 0.053454 | 0.56148
2019-12-17 | 0.87865 | 0.75717 | 0.36629 | 0.38925 | 0.050671 | 0.052513 | 0.822
2019-12-18 | 0.7408 | 0.66266 | 0.67046 | 0.66838 | 0.050366 | 0.051684 | 0.80144
2019-12-19 | 0.57338 | 0.56708 | 0.71317 | 0.71507 | 0.050366 | 0.050366 | 0.86537
2019-12-20 | 0.56543 | 0.50059 | 0.67229 | 0.66706 | 0.050366 | 0.050366 | 0.74728
2019-12-21 | 0.5313 | 0.52908 | 0.68676 | 0.69299 | 0.050348 | 0.050366 | 0.69836
2019-12-22 | 0.5157 | 0.5206 | 0.67412 | 0.67773 | 0.050366 | 0.050366 | 0.73129
2019-12-23 | 0.49175 | 0.58177 | 0.66635 | 0.64682 | 0.050383 | 0.052876 | 0.69285
2019-12-24 | 0.55169 | 0.57102 | 0.7024 | 0.6658 | 0.050451 | 0.054424 | 0.62237
2019-12-25 | 0.53537 | 0.54151 | 0.71404 | 0.68584 | 0.050993 | 0.054043 | 0.73995
2019-12-26 | 0.57227 | 0.58039 | 0.67191 | 0.64269 | 0.053631 | 0.06435 | 0.72128
2019-12-27 | 0.49861 | 0.50839 | 0.70961 | 0.6787 | 0.0572 | 0.069674 | 0.53681
2019-12-28 | 0.48492 | 0.48531 | 0.67395 | 0.63581 | 0.058437 | 0.073486 | 0.73338
2019-12-29 | 0.47348 | 0.47817 | 0.71743 | 0.68516 | 0.058458 | 0.069326 | 0.69789
2019-12-30 | 0.46506 | 0.41676 | 0.71125 | 0.67157 | 0.058675 | 0.071787 | 0.15866
2019-12-31 | 0.50466 | 0.46921 | 0.66116 | 0.66115 | 0.055398 | 0.068024 | 0.14501
2020-01-01 | 0.53414 | 0.54451 | 0.63747 | 0.68629 | 0.057075 | 0.069442 | 0.14306
2020-01-02 | 0.49852 | 0.51023 | 0.6225 | 0.67579 | 0.058338 | 0.069108 | 0.14452
2020-01-03 | 0.54652 | 0.57103 | 0.63396 | 0.68508 | 0.063739 | 0.074381 | 0.16894
2020-01-04 | 0.18546 | 0.18314 | 0.65924 | 0.69376 | 0.057797 | 0.068509 | 0.14879
2020-01-05 | 0.079331 | 0.053175 | 0.64649 | 0.69532 | 0.05567 | 0.070575 | 0.17289
2020-01-06 | 0.364 | 0.34341 | 0.67098 | 0.70794 | 0.059526 | 0.070118 | 0.42797
2020-01-07 | 0.5386 | 0.58065 | 0.65447 | 0.68086 | 0.065112 | 0.074139 | 0.73626
2020-01-08 | 0.59805 | 0.56271 | 0.67011 | 0.70109 | 0.060028 | 0.074512 | 0.77517
2020-01-09 | 0.57041 | 0.6242 | 0.64574 | 0.66361 | 0.062783 | 0.074761 | 0.7409
2020-01-10 | 0.5655 | 0.56591 | 0.67238 | 0.69415 | 0.066391 | 0.074786 | 0.65901
2020-01-11 | 0.56418 | 0.58944 | 0.66219 | 0.67556 | 0.068572 | 0.074786 | 0.51045
2020-01-12 | 0.56875 | 0.59929 | 0.6749 | 0.69671 | 0.06899 | 0.074769 | 0.54137
2020-01-13 | 0.5857 | 0.62282 | 0.65878 | 0.68168 | 0.062973 | 0.072957 | 0.64331
2020-01-14 | 0.61648 | 0.49908 | 0.70203 | 0.68506 | 0.052301 | 0.058557 | 0.61493
2020-01-15 | 0.5814 | 0.6762 | 0.77341 | 0.67904 | 0.053981 | 0.054189 | 0.54059
2020-01-16 | 0.5706 | 0.55902 | 0.7718 | 0.67582 | 0.050366 | 0.048811 | 0.72829
2020-01-17 | 0.51804 | 0.55363 | 0.80903 | 0.70899 | 0.051189 | 0.050366 | 0.76029
2020-01-18 | 0.62576 | 0.68091 | 0.79242 | 0.67872 | 0.051214 | 0.050366 | 0.76086
2020-01-19 | 0.60651 | 0.75072 | 0.79911 | 0.68967 | 0.055663 | 0.050366 | 0.78632
2020-01-20 | 0.57471 | 0.45575 | 0.80234 | 0.69285 | 0.058447 | 0.050366 | 0.76908
2020-01-21 | 0.59041 | 0.6041 | 0.77664 | 0.66831 | 0.066369 | 0.05062 | 0.76972
2020-01-22 | 0.56279 | 0.58768 | 0.80602 | 0.68605 | 0.071431 | 0.052467 | 0.7858
2020-01-23 | 0.35692 | 0.35868 | 0.77433 | 0.64767 | 0.070343 | 0.050366 | 0.51194
2020-01-24 | 0.43153 | 0.48551 | 0.7918 | 0.68878 | 0.071585 | 0.050366 | 0.47578
2020-01-25 | 0.60091 | 0.6331 | 0.78577 | 0.68236 | 0.072275 | 0.051315 | 0.80253
2020-01-26 | 0.58945 | 0.63552 | 0.816 | 0.70088 | 0.072782 | 0.054631 | 0.77447
2020-01-27 | 0.56102 | 0.588 | 0.79611 | 0.6821 | 0.074668 | 0.058777 | 0.60607
2020-01-28 | 0.58997 | 0.61668 | 0.80472 | 0.68861 | 0.074752 | 0.059315 | 0.83182
2020-01-29 | 0.58758 | 0.58857 | 0.79434 | 0.6703 | 0.074685 | 0.060952 | 0.7829
2020-01-30 | 0.56059 | 0.51371 | 0.74011 | 0.62609 | 0.074311 | 0.056594 | 0.35753
2020-01-31 | 0.59171 | 0.66731 | 0.70703 | 0.59887 | 0.073847 | 0.055692 | 0.42533
2020-02-01 | 0.494 | 0.50309 | 0.62115 | 0.5089 | 0.074515 | 0.055644 | 0.72439
2020-02-02 | 0.6083 | 0.54385 | 0.49011 | 0.45509 | 0.07465 | 0.058521 | 0.44564
2020-02-03 | 0.60839 | 0.57613 | 0.80561 | 0.66603 | 0.074345 | 0.056293 | 0.49051
2020-02-04 | 0.5743 | 0.4866 | 0.79077 | 0.64862 | 0.071247 | 0.064057 | 0.47833
2020-02-05 | 0.59421 | 0.75133 | 0.70871 | 0.54922 | 0.065063 | 0.074786 | 0.76546
2020-02-06 | 0.65554 | 0.53329 | 0.50225 | 0.44145 | 0.06415 | 0.078732 | 0.76761
2020-02-07 | 0.55028 | 0.11392 | 0.78772 | 0.65517 | 0.067596 | 0.074786 | 0.766
2020-02-08 | 0.51272 | 0.072523 | 0.76288 | 0.62116 | 0.073226 | 0.074786 | 0.77534
2020-02-09 | 0.51291 | 0.073901 | 0.64439 | 0.51881 | 0.074176 | 0.074786 | 0.76676
2020-02-10 | 0.51276 | 0.26109 | 0.56473 | 0.46651 | 0.07448 | 0.074786 | 0.49695
2020-02-11 | 0.63731 | 0.64351 | 0.75455 | 0.58968 | 0.068645 | 0.074858 | 0.54034
2020-02-12 | 0.73423 | 0.79705 | 0.63344 | 0.52383 | 0.070445 | 0.074786 | 0.70652
2020-02-13 | 0.71549 | 0.74641 | 0.58283 | 0.44494 | 0.07331 | 0.074786 | 0.7684
2020-02-14 | 0.71813 | 0.76388 | 0.52995 | 0.4667 | 0.073494 | 0.074786 | 0.75783
2020-02-15 | 0.74357 | 0.77962 | 0.84745 | 0.68491 | 0.074667 | 0.079064 | 0.77352
2020-02-16 | 0.73636 | 0.7573 | 0.80627 | 0.64236 | 0.074786 | 0.087069 | 0.78119
2020-02-17 | 0.61471 | 0.67555 | 0.70442 | 0.53905 | 0.070728 | 0.082917 | 0.79316
2020-02-18 | 0.52569 | 0.46938 | 0.73339 | 0.65295 | 0.059472 | 0.074786 | 0.78361
2020-02-19 | 0.52249 | 0.57312 | 0.81492 | 0.67733 | 0.050366 | 0.074682 | 0.75969
2020-02-20 | 0.5776 | 0.5922 | 0.6097 | 0.50943 | 0.050348 | 0.06897 | 0.7621
2020-02-21 | 0.59287 | 0.69996 | 0.8367 | 0.67914 | 0.050519 | 0.074786 | 0.77146
2020-02-22 | 0.52683 | 0.48801 | 0.8064 | 0.65897 | 0.054159 | 0.074786 | 0.76801
2020-02-23 | 0.57685 | 0.58293 | 0.71791 | 0.55066 | 0.052641 | 0.074786 | 0.69164
2020-02-24 | 0.62081 | 0.63799 | 0.57819 | 0.53097 | 0.050366 | 0.066422 | 0.77983
2020-02-25 | 0.63906 | 0.64943 | 0.61516 | 0.5728 | 0.050366 | 0.071067 | 0.46131
2020-02-26 | 0.63684 | 0.66336 | 0.7091 | 0.64769 | 0.050516 | 0.074786 | 0.75781
2020-02-27 | 0.62559 | 0.6513 | 0.71185 | 0.67358 | 0.050537 | 0.074786 | 0.77216
2020-02-28 | 0.6255 | 0.63387 | 0.59182 | 0.5156 | 0.050366 | 0.074786 | 0.77052
2020-02-29 | 0.6279 | 0.68279 | 0.49116 | 0.49598 | 0.050654 | 0.074786 | 0.77786
2020-03-01 | 0.65098 | 0.66552 | 0.53675 | 0.49354 | 0.050681 | 0.074786 | 0.76766
2020-03-02 | 0.63061 | 0.62688 | 0.83948 | 0.72203 | 0.060078 | 0.082551 | 0.7738
2020-03-03 | 0.592 | 0.61846 | 0.47353 | 0.17091 | 0.071177 | 0.080475 | 0.7771
2020-03-04 | 0.62835 | 0.61753 | 1.1358 | 0.063666 | 0.06734 | 0.077754 | 0.78569
2020-03-05 | 0.61116 | 0.60308 | 2.1808 | 0.065932 | 0.066485 | 1.4394 | 0.76905
2020-03-06 | 0.56058 | 0.55633 | 0.31673 | 0.34616 | 0.062425 | 5 | 0.77368 | MAV exceeded
2020-03-07 | 0.55163 | 0.51146 | 0.69667 | 0.64809 | 0.055674 | 5 | 0.78077 | MAV exceeded
2020-03-08 | 0.559 | 0.55795 | 0.59055 | 0.5533 | 0.060162 | 5 | 0.7669 | MAV exceeded
2020-03-09 | 0.59143 | 0.63359 | 0.6886 | 0.64022 | 0.065013 | 5 | 2.3444 | MAV exceeded
2020-03-10 | 0.58309 | 0.57878 | 0.70423 | 0.67128 | 0.065731 | 5 | 5 | MAV exceeded
2020-03-11 | 0.54297 | 0.52299 | 0.74034 | 0.6869 | 0.064258 | 5 | 4.9906 | MAV exceeded
2020-03-12 | 0.52836 | 0.54454 | 0.72175 | 0.6643 | 0.063976 | 5 | 4.9922 | MAV exceeded
2020-03-13 | 0.58269 | 0.62793 | 0.70819 | 0.68175 | 0.068908 | 5 | 4.9922 | MAV exceeded
2020-03-14 | 0.58585 | 0.55062 | 0.6727 | 0.65746 | 0.074786 | 5 | 4.9922 | MAV exceeded
2020-03-15 | 0.58746 | 0.59633 | 0.60246 | 0.62171 | 0.074786 | 5 | 4.9922 | MAV exceeded
2020-03-16 | 0.585 | 0.5908 | 0.6356 | 0.59797 | 0.074786 | 5 | 4.9408 | MAV exceeded
2020-03-17 | 0.3427 | 0.10126 | 0.77385 | 0.6148 | 0.074786 | 5 | 5 | MAV exceeded
2020-03-18 | 0.34462 | 0.28553 | 0.10101 | 0.085926 | 0.074804 | 5 | 2.9516 | MAV exceeded
2020-03-19 | 0.57869 | 0.60138 | 0.066128 | 0.062791 | 0.077679 | 5 | 0.78307 | MAV exceeded
2020-03-20 | 0.57446 | 0.67621 | 0.066124 | 0.062211 | 0.084935 | 5 | 0.79277 | MAV exceeded
2020-03-21 | 0.56433 | 0.59483 | 0.064427 | 0.061454 | 0.089105 | 5 | 0.76926 | MAV exceeded
2020-03-22 | 0.56852 | 0.59706 | 0.065759 | 0.061032 | 0.095394 | 5 | 0.74812 | MAV exceeded
2020-03-23 | 0.56911 | 0.55166 | 0.06184 | 0.058545 | 0.084924 | 5 | 0.73112 | MAV exceeded
2020-03-24 | 0.58108 | 0.54754 | 0.056632 | 0.056609 | 0.071988 | 5 | 0.80416 | MAV exceeded
2020-03-25 | 0.58476 | 0.58644 | 0.056584 | 0.052706 | 0.064146 | 4.9999 | 0.78194 | MAV exceeded
2020-03-26 | 0.59169 | 0.56676 | 0.051461 | 0.049352 | 0.054656 | 5 | 0.79512 | MAV exceeded
2020-03-27 | 0.60398 | 0.55527 | 0.056498 | 0.05268 | 0.059179 | 5 | 0.78716 | MAV exceeded
2020-03-28 | 0.68175 | 0.80646 | 0.060486 | 0.056467 | 0.057975 | 4.9988 | 0.77704 | MAV exceeded
2020-03-29 | 0.69888 | 0.71662 | 0.063287 | 0.06099 | 0.063653 | 4.9955 | 0.39807 | MAV exceeded
2020-03-30 | 0.56735 | 0.54976 | 0.053264 | 0.051423 | 0.050529 | 4.9979 | 0.75065 | MAV exceeded
2020-03-31 | 0.65527 | 0.70355 | 0.085061 | 0.072601 | 0.052098 | 4.9995 | 0.74538 | MAV exceeded
2020-04-01 | 0.62397 | 0.71943 | 0.30838 | 0.28865 | 0.057413 | 4.9988 | 0.6613 | MAV exceeded
2020-04-02 | 0.65422 | 0.66708 | 0.70581 | 0.55337 | 0.065741 | 5 | 0.38649 | MAV exceeded
2020-04-03 | 0.72236 | 0.7532 | 0.50222 | 0.34443 | 0.071864 | 4.9999 | 0.74244 | MAV exceeded
2020-04-04 | 0.68246 | 0.69384 | 0.062259 | 0.055834 | 0.074786 | 5 | 0.77792 | MAV exceeded
2020-04-05 | 0.74588 | 0.72023 | 0.068351 | 0.060204 | 0.074583 | 4.9999 | 0.81913 | MAV exceeded
2020-04-05 23:00 | 0.67985 | 0.64037 | 0.065265 | 0.056856 | 0.074377 | 5 | 0.62855 | MAV exceeded
2020-04-06 23:00 | 0.69111 | 0.6862 | 0.068135 | 0.059063 | 0.074786 | 5 | 0.93973 | MAV exceeded
2020-04-07 23:00 | 0.69328 | 0.70217 | 0.071308 | 0.061421 | 0.074514 | 5 | 0.77727 | MAV exceeded
2020-04-08 23:00 | 0.60037 | 0.59384 | 0.070891 | 0.060976 | 0.074583 | 5 | 0.77319 | MAV exceeded
2020-04-09 23:00 | 0.64589 | 0.59245 | 0.067156 | 0.059022 | 0.068816 | 4.997 | 0.78609 | MAV exceeded
2020-04-10 23:00 | 0.70134 | 0.68139 | 0.065143 | 0.057715 | 0.065022 | 4.9972 | 0.79639 | MAV exceeded
2020-04-11 23:00 | 0.70346 | 0.71024 | 0.067704 | 0.059232 | 0.071428 | 4.9999 | 0.71085 | MAV exceeded
2020-04-12 23:00 | 0.70617 | 0.73641 | 0.074425 | 0.06328 | 0.07348 | 5 | 0.73729 | MAV exceeded
2020-04-13 23:00 | 0.6973 | 0.61826 | 0.071278 | 0.062101 | 0.061209 | 4.9993 | 0.74359 | MAV exceeded
2020-04-14 23:00 | 0.72053 | 0.74112 | 0.056387 | 0.052514 | 0.056305 | 4.9955 | 0.78643 | MAV exceeded
2020-04-15 23:00 | 0.72729 | 0.72787 | 0.056717 | 0.053595 | 0.062571 | 4.9959 | 0.7863 | MAV exceeded
2020-04-16 23:00 | 0.72158 | 0.79124 | 0.063352 | 0.057356 | 0.070126 | 4.9989 | 0.76262 | MAV exceeded
2020-04-17 23:00 | 0.70478 | 0.70571 | 0.066993 | 0.05885 | 0.07426 | 4.9993 | 0.79119 | MAV exceeded
2020-04-18 23:00 | 0.73597 | 0.72846 | 0.064693 | 0.060367 | 0.074365 | 4.9993 | 0.79579 | MAV exceeded
2020-04-19 23:00 | 0.70732 | 0.60163 | 0.059127 | 0.055261 | 0.073495 | 4.9997 | 0.54066 | MAV exceeded
2020-04-20 23:00 | 0.74656 | 0.7561 | 0.052813 | 0.049674 | 0.074148 | 4.9989 | 0.77672 | MAV exceeded
2020-04-21 23:00 | 0.88329 | 0.90243 | 0.050308 | 0.049284 | 0.074597 | 4.9973 | 0.76619 | MAV exceeded
2020-04-22 23:00 | 0.8143 | 0.92474 | 0.056025 | 0.051805 | 0.074786 | 4.9995 | 0.72211 | MAV exceeded
2020-04-23 23:00 | 0.76778 | 0.78152 | 0.06195 | 0.055044 | 0.074786 | 4.9999 | 0.75086 | MAV exceeded
2020-04-24 23:00 | 0.6934 | 0.68676 | 0.065319 | 0.05606 | 0.074786 | 4.9991 | 0.78703 | MAV exceeded
2020-04-25 23:00 | 0.70342 | 0.69275 | 0.066913 | 0.056688 | 0.074786 | 4.9995 | 0.75818 | MAV exceeded
2020-04-26 23:00 | 0.67743 | 0.68722 | 0.068865 | 0.058503 | 0.074786 | 4.9999 | 0.67584 | MAV exceeded
2020-04-27 23:00 | 0.6901 | 0.6824 | 0.071701 | 0.060447 | 0.074657 | 4.9996 | 0.12914 | MAV exceeded
2020-04-28 23:00 | 0.72832 | 0.65543 | 0.070018 | 0.05994 | 0.069843 | 4.9959 | 0.097767 | MAV exceeded
2020-04-29 23:00 | 0.74829 | 0.73713 | 0.066765 | 0.058423 | 0.072601 | 4.9972 | 0.38196 | MAV exceeded
2020-04-30 23:00 | 0.74134 | 0.71342 | 0.070473 | 0.060787 | 0.074735 | 4.999 | 0.71241 | MAV exceeded
2020-05-01 23:00 | 0.51674 | 0.51785 | 0.071799 | 0.061339 | 0.074786 | 4.9998 | 0.62869 | MAV exceeded
2020-05-02 23:00 | 0.741 | 0.81524 | 0.076384 | 0.061195 | 0.074786 | 5 | 0.78103 | MAV exceeded
2020-05-03 23:00 | 0.84788 | 0.93752 | 0.07881 | 0.061715 | 0.074786 | 5 | 0.79264 | MAV exceeded
2020-05-04 23:00 | 0.76745 | 0.73206 | 0.075032 | 0.060741 | 0.075453 | 4.9974 | 0.79329 | MAV exceeded
2020-05-05 23:00 | 0.80913 | 0.78469 | 0.069613 | 0.057732 | 0.079987 | 4.9921 | 0.78692 | MAV exceeded
2020-05-06 23:00 | 0.71076 | 0.6674 | 0.053297 | 0.047863 | 0.074366 | 4.9906 | 0.71861 | MAV exceeded
2020-05-07 23:00 | 0.7671 | 0.77388 | 0.056975 | 0.050217 | 0.052982 | 4.9913 | 0.71507 | MAV exceeded
2020-05-08 23:00 | 0.70092 | 0.73324 | 0.059921 | 0.052417 | 0.061278 | 4.9927 | 0.78726 | MAV exceeded
2020-05-09 23:00 | 0.69765 | 0.68902 | 0.063142 | 0.053923 | 0.062974 | 4.992 | 0.78638 | MAV exceeded
2020-05-10 23:00 | 0.67593 | 0.64189 | 0.067229 | 0.05625 | 0.067877 | 4.9936 | 0.7846 | MAV exceeded
2020-05-11 23:00 | 0.67454 | 0.67112 | 0.070455 | 0.058077 | 0.072112 | 4.9945 | 0.78292 | MAV exceeded
2020-05-12 23:00 | 0.63246 | 0.6055 | 0.071066 | 0.059143 | 0.073201 | 4.9931 | 0.78434 | MAV exceeded
2020-05-13 23:00 | 0.68323 | 0.6918 | 0.069001 | 0.059551 | 0.073896 | 4.9926 | 0.78346 | MAV exceeded
2020-05-14 23:00 | 0.68513 | 0.67374 | 0.071687 | 0.060368 | 0.073918 | 4.9926 | 0.78388 | MAV exceeded
2020-05-15 23:00 | 0.65802 | 0.66012 | 0.074061 | 0.06178 | 0.074343 | 4.9919 | 0.79305 | MAV exceeded
2020-05-16 23:00 | 0.67319 | 0.68326 | 0.073711 | 0.061354 | 0.074453 | 4.9915 | 0.79929 | MAV exceeded
2020-05-17 23:00 | 0.63499 | 0.62754 | 0.074555 | 0.062469 | 0.074379 | 4.9898 | 0.78426 | MAV exceeded
2020-05-18 23:00 | 0.68539 | 0.66448 | 0.075327 | 0.062816 | 0.07366 | 4.992 | 0.78261 | MAV exceeded
2020-05-19 23:00 | 0.68903 | 0.67355 | 0.093315 | 0.079861 | 0.070664 | 4.9857 | 0.78495 | MAV exceeded
2020-05-20 23:00 | 0.69535 | 0.67837 | 0.070265 | 0.060827 | 0.071457 | 4.9855 | 0.56964 | MAV exceeded
2020-05-21 23:00 | 0.72448 | 0.71754 | 0.074592 | 0.062964 | 0.070865 | 4.9912 | 0.12063 | MAV exceeded
2020-05-22 23:00 | 0.72912 | 0.72779 | 0.07704 | 0.063752 | 0.066475 | 4.9924 | 0.097957 | MAV exceeded
2020-05-23 23:00 | 0.72391 | 0.71604 | 0.077034 | 0.06365 | 0.065184 | 4.9924 | 0.11071 | MAV exceeded
2020-05-24 23:00 | 0.84607 | 0.83646 | 0.079582 | 0.066238 | 0.067858 | 4.9923 | 0.10652 | MAV exceeded
2020-05-25 23:00 | 0.8625 | 0.81925 | 0.075991 | 0.063105 | 0.073073 | 4.9927 | 0.10138 | MAV exceeded
2020-05-26 23:00 | 0.7511 | 0.74078 | 0.061693 | 0.087667 | 0.068718 | 4.9923 | 0.10333 | MAV exceeded
2020-05-27 23:00 | 0.65903 | 0.64286 | 0.090178 | 0.06178 | 0.065629 | 4.9913 | 0.11688 | MAV exceeded
2020-05-28 23:00 | 0.64436 | 0.63095 | 0.26573 | 0.20617 | 0.06988 | 4.9901 | 0.10104 | MAV exceeded
2020-05-29 23:00 | 0.65138 | 0.61824 | 0.068294 | 0.058146 | 0.074034 | 4.9922 | 0.10119 | MAV exceeded
2020-05-30 23:00 | 0.73189 | 0.7374 | 0.07062 | 0.060484 | 0.074192 | 4.992 | 0.10247 | MAV exceeded
2020-05-31 23:00 | 0.74998 | 0.73828 | 0.071082 | 0.060763 | 0.073838 | 4.9922 | 0.099049 | MAV exceeded
2020-06-01 23:00 | 0.73928 | 0.7606 | 0.33463 | 0.24577 | 0.069029 | 4.9942 | 0.09324 | MAV exceeded
2020-06-02 23:00 | 0.70897 | 0.71086 | 0.33955 | 0.24393 | 0.06793 | 4.9933 | 0.097085 | MAV exceeded
2020-06-03 23:00 | 0.73648 | 0.74086 | 0.44879 | 0.39269 | 0.074497 | 4.9947 | 0.097389 | MAV exceeded
2020-06-04 23:00 | 0.83715 | 0.81394 | 0.68323 | 0.5653 | 0.070967 | 4.9949 | 0.097165 | MAV exceeded
2020-06-05 23:00 | 0.8638 | 0.86258 | 0.32614 | 0.25826 | 0.07333 | 4.993 | 0.093738 | MAV exceeded
2020-06-06 23:00 | 0.84204 | 0.84096 | 0.28423 | 0.2873 | 0.074786 | 4.9929 | 0.095707 | MAV exceeded
2020-06-07 23:00 | 0.84366 | 0.8356 | 0.69123 | 0.60508 | 0.070187 | 4.9924 | 0.12599 | MAV exceeded
2020-06-08 23:00 | 0.83175 | 0.82937 | 0.68501 | 0.53765 | 0.067418 | 4.991 | 0.096305 | MAV exceeded
2020-06-09 23:00 | 0.80938 | 0.79488 | 0.72008 | 0.66443 | 0.068392 | 4.9876 | 0.096306 | MAV exceeded
2020-06-10 23:00 | 0.77874 | 0.80027 | 0.80125 | 0.64417 | 0.069595 | 4.9847 | 0.096306 | MAV exceeded
2020-06-11 23:00 | 0.64311 | 0.63373 | 0.75336 | 0.64885 | 0.073686 | 4.991 | 0.096305 | MAV exceeded
2020-06-12 23:00 | 0.7059 | 0.71141 | 0.64752 | 0.64137 | 0.074786 | 4.9913 | 0.096305 | MAV exceeded
2020-06-13 23:00 | 0.64905 | 0.63559 | 0.6357 | 0.63263 | 0.074804 | 4.9851 | 0.096317 | MAV exceeded
2020-06-14 23:00 | 0.59623 | 0.61459 | 0.69138 | 0.6454 | 0.074058 | 4.9853 | 0.09125 | MAV exceeded
2020-06-15 23:00 | 0.57041 | 0.56632 | 0.70058 | 0.57391 | 0.072903 | 4.991 | 0.094087 | MAV exceeded
2020-06-16 23:00 | 0.62537 | 0.63831 | 0.53015 | 0.45831 | 0.069993 | 4.994 | 0.089621 | MAV exceeded
2020-06-17 23:00 | 0.67363 | 0.672 | 0.64611 | 0.58497 | 0.074427 | 4.996 | 0.088284 | MAV exceeded
2020-06-18 23:00 | 0.69037 | 0.69877 | 0.79258 | 0.6709 | 0.074753 | 4.9942 | 0.087191 | MAV exceeded
2020-06-19 23:00 | 0.76583 | 0.77314 | 0.82071 | 0.68658 | 0.074786 | 4.9929 | 0.088863 | MAV exceeded
2020-06-20 23:00 | 0.8977 | 0.90124 | 0.78119 | 0.65686 | 0.074786 | 4.9924 | 0.090401 | MAV exceeded
2020-06-21 23:00 | 0.86518 | 0.88081 | 0.74284 | 0.62571 | 0.074786 | 4.9894 | 0.089402 | MAV exceeded
2020-06-22 23:00 | 0.80023 | 0.80726 | 0.66728 | 0.53203 | 0.073105 | 4.9862 | 0.086839 | MAV exceeded
2020-06-23 23:00 | 0.43639 | 0.44028 | 0.73382 | 0.62903 | 0.068944 | 4.985 | 0.095058 | MAV exceeded
2020-06-24 23:00 | 0.16533 | 0.15742 | 0.73145 | 0.60724 | 0.073546 | 4.9893 | 0.090157 | MAV exceeded
2020-06-25 23:00 | 0.71336 | 0.72299 | 0.67707 | 0.54717 | 0.074306 | 4.9915 | 0.090404 | MAV exceeded
2020-06-26 23:00 | 0.88952 | 0.88963 | 0.41617 | 0.39154 | 0.074786 | 4.9924 | 0.092526 | MAV exceeded
2020-06-27 23:00 | 0.90402 | 0.88343 | 0.72783 | 0.61648 | 0.074786 | 4.9926 | 0.089727 | MAV exceeded
2020-06-28 23:00 | 0.85526 | 0.84203 | 0.45925 | 0.42406 | 0.068879 | 4.9921 | 0.11397 | MAV exceeded
2020-06-29 23:00 | 0.55611 | 0.55696 | 0.65371 | 0.57969 | 0.054512 | 4.9897 | 0.10392 | MAV exceeded
2020-06-30 23:00 | 0.64856 | 0.6437 | 0.5179 | 0.47103 | 0.047924 | 4.985 | 0.094435 | MAV exceeded

## 20-21
Date Stamp | .Gear Island 1050 Fluoride | .Gear Island 1050 Fluoride Analyser #2 | .Te Marua PS Fluoride Residual | .Te Marua TP Fluoride Residual | .Wainui Fluoride Building Fluoride Residual Stream 1 | .Wainui Fluoride Building Fluoride Residual Stream 2 | .Waterloo Naenae Fluoride Residual
2020-07-01 23:00 | 0.51318 | 0.53722 | 0.73106 | 0.63241 | 0.045812 | 4.983 | 0.095662
2020-07-02 23:00 | 0.50912 | 0.49729 | 0.71484 | 0.60698 | 0.047499 | 4.983 | 0.095524
2020-07-03 23:00 | 0.70616 | 0.67713 | 0.45631 | 0.93333 | 0.050366 | 4.9835 | 0.096324
2020-07-04 23:00 | 0.7 | 0.66323 | 0.44077 | 0.41394 | 0.051516 | 4.9836 | 0.096579
2020-07-05 23:00 | 0.68476 | 0.68089 | 0.7766 | 0.6673 | 0.056734 | 4.9854 | 0.096705
2020-07-06 23:00 | 0.62992 | 0.6274 | 0.77587 | 0.67723 | 0.059132 | 4.9876 | 0.097157 |  | Fluoride not dosed
2020-07-07 23:00 | 0.57447 | 0.57535 | 0.76759 | 0.66855 | 0.057138 | 4.9852 | 0.097947 |  | fluoride dosed but outside recommended range
2020-07-08 23:00 | 0.72302 | 0.71838 | 0.77401 | 0.66841 | 0.0484 | 4.9829 | 0.096985 |  | Fluoride dosed but within recommended range
2020-07-09 23:00 | 0.74851 | 0.76109 | 0.77063 | 0.66384 | 0.051384 | 4.9833 | 0.096037
2020-07-10 23:00 | 0.85984 | 0.84348 | 0.65464 | 0.5751 | 0.058952 | 4.9837 | 0.090543 | Assumptions: |  | 1. Values less than 0.1 indicates that fluoride is not being dosed
2020-07-11 23:00 | 0.85847 | 0.85113 | 0.77203 | 0.67281 | 0.062719 | 4.9838 | 0.091937 |  |  | 2. MAV exceedences are due to the default value that the analyser goes to when fluoride dosing is ceased
2020-07-12 23:00 | 0.81302 | 0.77582 | 0.73654 | 0.63717 | 0.06105 | 4.9853 | 0.094331 |  |  | 3. The Gear Island sampling point is downstream of the plant and can contain a residual from the Wainuiomata WTP
2020-07-13 23:00 | 0.47675 | 0.46657 | 0.76072 | 0.65918 | 0.054943 | 4.9833 | 0.097902
2020-07-14 23:00 | 0.45142 | 0.43569 | 0.76421 | 0.66399 | 0.05856 | 4.9828 | 0.099581
2020-07-15 23:00 | 0.65895 | 0.6489 | 0.72217 | 0.62458 | 0.062994 | 4.9825 | 0.10311
2020-07-16 23:00 | 0.58353 | 0.58885 | 0.65673 | 0.56459 | 0.06128 | 4.9823 | 0.09849
2020-07-17 23:00 | 0.85555 | 0.8623 | 0.7653 | 0.64438 | 0.063813 | 4.6815 | 0.098198
2020-07-18 23:00 | 0.83304 | 0.86573 | 0.79827 | 0.67566 | 0.069909 | 4.9836 | 0.10238
2020-07-19 23:00 | 0.28014 | 0.70215 | 0.81655 | 0.69372 | 0.071459 | 4.9837 | 0.11481
2020-07-20 23:00 | 0.58531 | 0.36592 | 0.85089 | 0.72101 | 0.071027 | 4.9849 | 0.097632
2020-07-21 23:00 | 0.70462 | 0.69273 | 0.75921 | 0.66598 | 0.063485 | 4.9833 | 0.095921
2020-07-22 23:00 | 0.28695 | 0.27472 | 0.8309 | 0.68853 | 0.055516 | 4.983 | 0.097662
2020-07-23 23:00 | 0.44178 | 0.40932 | 0.82324 | 0.69805 | 0.064018 | 4.0108 | 0.095753
2020-07-24 23:00 | 1.0376 | 0.12199 | 0.81529 | 0.69398 | 0.066508 | 2.4684 | 0.095109
2020-07-25 23:00 | 3.3653 | 0.86102 | 0.71695 | 0.59488 | 0.074692 | 4.2991 | 0.093794
2020-07-26 23:00 | 2.1808 | 0.56507 | 0.64161 | 0.67207 | 0.073828 | 4.9765 | 0.10757
2020-07-27 23:00 | 0.49445 | 0.42949 | 0.78558 | 0.68107 | 0.071609 | 4.9757 | 0.093505
2020-07-28 23:00 | 0.72419 | 0.70069 | 0.80283 | 0.68997 | 0.071535 | 4.9772 | 0.094018
2020-07-29 23:00 | 0.60755 | 0.60531 | 0.79811 | 0.67994 | 0.073246 | 4.977 | 0.094358
2020-07-30 23:00 | 0.57177 | 0.57591 | 0.77558 | 0.67226 | 0.073778 | 4.9783 | 0.094741
2020-07-31 23:00 | 0.59028 | 0.59144 | 0.81216 | 0.69423 | 0.074326 | 4.6329 | 0.098653
2020-08-01 23:00 | 0.57689 | 0.57999 | 0.78878 | 0.68916 | 0.074157 | 2.7035 | 0.095049
2020-08-02 23:00 | 0.59296 | 0.60023 | 0.82754 | 0.71577 | 0.074592 | 3.8852 | 0.10287
2020-08-03 23:00 | 0.52462 | 0.53028 | 0.81945 | 0.70574 | 0.07493 | 4.9831 | 0.091127
2020-08-04 23:00 | 0.20904 | 0.21119 | 0.67808 | 0.56363 | 0.074804 | 4.9834 | 1.2406
2020-08-05 23:00 | 0.63457 | 0.63912 | 0.82776 | 0.70743 | 0.074786 | 4.9839 | 0.088661
2020-08-06 23:00 | 0.56155 | 0.55937 | 0.71838 | 0.62537 | 0.074736 | 4.9846 | 0.096643
2020-08-07 23:00 | 0.77033 | 0.76593 | 0.82958 | 0.71611 | 0.074753 | 4.9826 | 0.091592
2020-08-08 23:00 | 0.87876 | 0.87078 | 0.80656 | 0.69479 | 0.074803 | 4.9803 | 0.09005
2020-08-09 23:00 | 0.86896 | 0.8754 | 0.82604 | 0.71001 | 0.074786 | 4.9794 | 0.088301
2020-08-10 23:00 | 0.87474 | 0.86983 | 0.74304 | 0.64535 | 0.074822 | 4.9816 | 0.088511
2020-08-11 23:00 | 0.79385 | 0.79344 | 0.80795 | 0.69441 | 0.074826 | 4.9829 | 0.090902
2020-08-12 23:00 | 0.59918 | 0.6011 | 0.80119 | 0.6894 | 0.072399 | 4.9796 | 0.092785
2020-08-13 23:00 | 0.59172 | 0.59222 | 0.81408 | 0.70127 | 0.074142 | 4.9815 | 0.10312
2020-08-14 23:00 | 0.53311 | 0.52591 | 0.81084 | 0.69582 | 0.072855 | 4.9781 | 0.089095
2020-08-15 23:00 | 0.3901 | 0.4979 | 0.81495 | 0.70564 | 0.072572 | 4.9521 | 0.093936
2020-08-16 23:00 | 0.58203 | 0.54465 | 0.77891 | 0.6814 | 0.074617 | 4.5389 | 0.1094
2020-08-17 23:00 | 0.67098 | 0.64844 | 0.78819 | 0.69062 | 0.073357 | 4.0054 | 0.08919
2020-08-18 23:00 | 0.72621 | 0.7131 | 0.76934 | 0.65637 | 0.073565 | 3.6171 | 0.081556
2020-08-19 23:00 | 0.70869 | 0.67583 | 0.78091 | 0.67318 | 0.074702 | 4.465 | 0.080466
2020-08-20 23:00 | 0.78942 | 0.75852 | 0.79971 | 0.68334 | 0.070508 | 4.9318 | 0.084108
2020-08-21 23:00 | 0.69323 | 0.63366 | 0.80479 | 0.69101 | 0.071995 | 4.9835 | 0.088466
2020-08-22 23:00 | 0.6818 | 0.63875 | 0.81247 | 0.70287 | 0.074532 | 4.9832 | 0.090943
2020-08-23 23:00 | 0.70335 | 0.65654 | 0.81555 | 0.69727 | 0.070626 | 4.9846 | 0.11263
2020-08-24 23:00 | 0.76703 | 0.24656 | 0.82683 | 0.69791 | 0.073231 | 4.9839 | 0.086558
2020-08-25 23:00 | 0.42644 | 0.42282 | 0.8204 | 0.68576 | 0.074786 | 4.5151 | 0.086908
2020-08-26 23:00 | 0.87731 | 0.86439 | 0.80402 | 0.68191 | 0.069868 | 1.9527 | 0.087405
2020-08-27 23:00 | 0.83557 | 0.84982 | 0.80974 | 0.69135 | 0.069709 | 2.7676 | 0.095488
2020-08-28 23:00 | 0.87286 | 0.86443 | 0.78142 | 0.66558 | 0.074786 | 4.3717 | 0.088231
2020-08-29 23:00 | 0.83255 | 0.82576 | 0.76078 | 0.649 | 0.074804 | 4.9958 | 0.088833
2020-08-30 23:00 | 0.75685 | 0.77689 | 0.77723 | 0.64974 | 0.075345 | 4.9983 | 0.092025
2020-08-31 23:00 | 0.57988 | 0.57565 | 0.78152 | 0.65691 | 0.07462 | 4.9979 | 0.092087
2020-09-01 23:00 | 0.7172 | 0.70832 | 0.70328 | 0.58538 | 0.071818 | 4.9927 | 0.091858
2020-09-02 23:00 | 0.59584 | 0.59614 | 0.59436 | 0.44344 | 0.0668 | 4.9917 | 0.092358
2020-09-03 23:00 | 0.54478 | 0.53468 | 0.63826 | 0.5622 | 0.066991 | 4.9907 | 0.093941
2020-09-04 23:00 | 0.52194 | 0.52905 | 0.6875 | 0.57181 | 0.072893 | 4.9923 | 0.09756
2020-09-05 23:00 | 0.5461 | 0.54401 | 0.77746 | 0.6413 | 0.073155 | 4.9926 | 0.097631
2020-09-06 23:00 | 0.81168 | 0.80974 | 0.7814 | 0.63596 | 0.064891 | 4.9932 | 0.093306
2020-09-07 23:00 | 0.55864 | 0.55624 | 0.75865 | 0.59203 | 0.062836 | 4.9935 | 0.095279
2020-09-08 23:00 | 0.56528 | 0.56455 | 0.47918 | 0.41953 | 0.07198 | 4.9955 | 0.098694
2020-09-09 23:00 | 0.61035 | 0.60937 | 0.68858 | 0.6235 | 0.0747 | 4.9953 | 0.097568
2020-09-10 23:00 | 0.5238 | 0.5216 | 0.55959 | 0.57011 | 0.050785 | 4.9922 | 0.097499
2020-09-11 23:00 | 0.41966 | 0.41555 | 0.76562 | 0.50798 | 0.053829 | 4.9921 | 0.098912
2020-09-12 23:00 | 0.63311 | 0.62319 | 0.89758 | 0.61264 | 0.068416 | 4.9943 | 0.098881
2020-09-13 23:00 | 0.38178 | 0.37925 | 0.62935 | 0.58779 | 0.074634 | 4.9959 | 0.09802
2020-09-14 23:00 | 0.42162 | 0.42246 | 0.38205 | 0.53417 | 0.074719 | 4.9992 | 0.095084
2020-09-15 23:00 | 0.39341 | 0.24315 | 0.46459 | 0.44933 | 0.074651 | 4.9993 | 0.0951
2020-09-16 23:00 | 0.30308 | 0.13574 | 0.33847 | 0.35817 | 0.074786 | 4.9998 | 0.095723
2020-09-17 23:00 | 0.3068 | 0.30984 | 0.35527 | 0.39274 | 0.063069 | 4.9977 | 0.096472
2020-09-18 23:00 | 0.26098 | 0.25059 | 0.092897 | 0.088151 | 0.057798 | 4.9951 | 0.097578
2020-09-19 23:00 | 0.29199 | 0.28298 | 0.60164 | 0.63408 | 0.071173 | 4.9957 | 0.097103
2020-09-20 23:00 | 0.30537 | 0.30226 | 0.60198 | 0.59821 | 0.074005 | 4.9958 | 0.12006
2020-09-21 23:00 | 0.32791 | 0.32984 | 0.6106 | 0.62553 | 0.069799 | 2.6051 | 0.094128
2020-09-22 23:00 | 0.42054 | 0.41407 | 0.53521 | 0.54866 | 0.27878 | 0.25564 | 0.11195
2020-09-23 23:00 | 0.57868 | 0.57677 | 0.52952 | 0.5468 | 0.049928 | 0.049711 | 0.091045
2020-09-24 23:00 | 0.54002 | 0.52763 | 0.39794 | 0.42105 | 0.29295 | 0.28527 | 0.10337
2020-09-25 23:00 | 0.46278 | 0.4521 | 0.59832 | 0.62667 | 0.058979 | 0.052604 | 0.29198
2020-09-26 23:00 | 0.7824 | 0.77971 | 0.57627 | 0.56859 | 0.064057 | 0.058143 | 0.22281
2020-09-28 | 0.62421 | 0.6103 | 0.46557 | 0.50164 | 0.41333 | 0.39967 | 0.22617
2020-09-29 | 0.80741 | 0.81483 | 0.59137 | 0.61015 | 0.83689 | 0.79706 | 0.24281
2020-09-30 | 0.80522 | 0.80693 | 0.59405 | 0.59153 | 0.81384 | 0.77516 | 0.24243
2020-10-01 | 0.75984 | 0.74861 | 0.57021 | 0.56293 | 0.48218 | 0.4545 | 0.23436
2020-10-02 | 0.63066 | 0.62901 | 0.55176 | 0.56281 | 0.37493 | 0.35256 | 0.068568
2020-10-03 | 0.69359 | 0.72252 | 0.65813 | 0.65789 | 0.43513 | 0.408 | 0.36723
2020-10-04 | 0.74981 | 0.81957 | 0.57012 | 0.55586 | 0.25252 | 0.23501 | 0.41969
2020-10-05 | 0.61154 | 0.70759 | 0.67754 | 0.6617 | 0.37286 | 0.34877 | 0.26636
2020-10-06 | 0.60849 | 0.60378 | 0.52255 | 0.51289 | 0.38227 | 0.36182 | 0.10879
2020-10-07 | 0.51346 | 0.5184 | 0.58784 | 0.50629 | 0.3723 | 0.35453 | 0.10328
2020-10-08 | 0.50297 | 0.48714 | 0.44869 | 0.49346 | 0.35429 | 0.33811 | 0.1024
2020-10-09 | 0.46321 | 0.45626 | 0.72311 | 0.67617 | 0.32583 | 0.31068 | 0.10073
2020-10-10 | 0.55687 | 0.53989 | 0.73055 | 0.68025 | 0.32997 | 0.31811 | 0.097824
2020-10-11 | 0.49285 | 0.46599 | 0.72707 | 0.67308 | 0.29971 | 0.28839 | 0.097056
2020-10-12 | 0.60208 | 0.60813 | 0.67648 | 0.62225 | 0.36388 | 0.35619 | 0.094412
2020-10-13 | 0.95301 | 0.29156 | 0.71048 | 0.6786 | 0.33701 | 0.3292 | 0.096436
2020-10-14 | 0.51823 | 0.41243 | 0.70704 | 0.66352 | 0.33296 | 0.32558 | 0.11743
2020-10-15 | 0.56467 | 0.52245 | 0.51671 | 0.458 | 0.35999 | 0.34758 | 0.097453
2020-10-16 | 0.46805 | 0.4201 | 0.70675 | 0.66488 | 0.2379 | 0.23071 | 0.096338
2020-10-17 | 0.07784 | 0.067684 | 0.67997 | 0.63844 | 0.066615 | 0.05492 | 0.099363
2020-10-18 | 0.079171 | 0.065899 | 0.7049 | 0.67381 | 0.066773 | 0.057117 | 0.099326
2020-10-19 | 0.080003 | 0.06831 | 0.61376 | 0.55628 | 0.068754 | 0.068884 | 0.10115
2020-10-20 | 0.086003 | 0.06946 | 0.68636 | 0.67778 | 0.090619 | 0.098554 | 0.097009
2020-10-21 | 0.086885 | 0.069082 | 0.65027 | 0.60776 | 0.067284 | 0.069457 | 0.09121
2020-10-22 | 0.084986 | 0.070973 | 0.67993 | 0.65423 | 0.069629 | 0.070512 | 0.094215
2020-10-23 | 0.080998 | 0.066949 | 0.57063 | 0.56402 | 0.071446 | 0.065019 | 0.092302
2020-10-24 | 0.084776 | 0.06971 | 0.59303 | 0.62688 | 0.073873 | 0.068957 | 0.089012
2020-10-25 | 0.084468 | 0.068931 | 0.65662 | 0.6753 | 0.0721 | 0.073667 | 0.097239
2020-10-26 | 0.081582 | 0.067812 | 0.65723 | 0.65795 | 0.068715 | 0.07326 | 0.091768
2020-10-27 | 0.081578 | 0.0691 | 0.42027 | 0.62618 | 0.057612 | 0.062242 | 0.2525
2020-10-28 | 4.0414 | 0.061009 | 0.277 | 0.6323 | 0.050074 | 0.050803 | 0.091952
2020-10-29 | 0.43949 | 0.057558 | 0.68587 | 0.70144 | 0.050429 | 0.051791 | 0.092835
2020-10-30 | 0.076749 | 0.062845 | 0.69252 | 0.68268 | 0.0504 | 0.0504 | 0.09831
2020-10-31 | 0.076446 | 0.064372 | 0.68723 | 0.67916 | 0.050468 | 0.052095 | 0.096584
2020-11-01 | 4.4679 | 0.074151 | 0.68703 | 0.65477 | 3.7366 | 0.012406 | 0.10039
2020-11-02 | 4.6013 | 0.077362 | 0.61166 | 0.53647 | 2.8842 | 2.6603 | 0.10287
2020-11-03 | 0.46558 | 0.073328 | 0.41551 | 0.41833 | 0.055667 | 0.058134 | 0.095144
2020-11-04 | 4.0107 | 0.072762 | 0.65915 | 0.59537 | 0.073496 | 0.074176 | 0.093928
2020-11-05 | 2.8531 | 0.076359 | 0.55429 | 0.51089 | 0.072756 | 0.071398 | 0.095323
2020-11-06 | 0.3036 | 0.22562 | 0.70235 | 0.64739 | 0.062805 | 0.063491 | 0.095852
2020-11-07 | 0.90028 | 0.32765 | 0.49577 | 0.45733 | 0.059959 | 0.062581 | 0.09919
2020-11-08 | 0.75984 | 0.52151 | 0.69407 | 0.64897 | 0.054235 | 0.057904 | 0.085488
2020-11-09 | 0.73498 | 0.64952 | 0.69402 | 0.63916 | 0.051492 | 0.054299 | 0.094568
2020-11-10 | 3.8786 | 0.68052 | 0.68802 | 0.64599 | 0.050366 | 0.050366 | 0.11766
2020-11-11 | 3.8914 | 0.65914 | 0.6632 | 0.63158 | 0.050186 | 0.05061 | 0.093171
2020-11-12 | 4.1619 | 0.46494 | 0.67924 | 0.62846 | 0.053306 | 0.058286 | 0.087533
2020-11-13 | 4.3214 | 0.37853 | 0.65992 | 0.60165 | 0.056612 | 0.069247 | 0.16295
2020-11-14 | 4.0603 | 0.33111 | 0.68922 | 0.62117 | 0.05956 | 0.073846 | 0.086237
2020-11-15 | 4.7971 | 0.38513 | 0.69929 | 0.63595 | 0.061602 | 0.074786 | 0.082017
2020-11-16 | 4.7234 | 0.37969 | 0.68993 | 0.63805 | 0.058187 | 0.073318 | 0.35087
2020-11-17 | 2.5207 | 0.28964 | 0.70177 | 0.64469 | 0.061124 | 0.074893 | 0.19758
2020-11-18 | 0.39865 | 0.39463 | 0.68639 | 0.63386 | 0.14952 | 0.18136 | 0.1841
2020-11-19 | 0.40314 | 0.38191 | 0.69064 | 0.65987 | 0.16053 | 0.19718 | 0.13993
2020-11-20 | 0.47818 | 0.45484 | 0.67422 | 0.59752 | 0.28584 | 0.35452 | 0.13972
2020-11-21 | 0.39364 | 0.34783 | 0.68685 | 0.60885 | 0.057704 | 0.073114 | 0.086721
2020-11-22 | 0.36519 | 0.3207 | 0.69497 | 0.61519 | 0.054284 | 0.074786 | 0.086526
2020-11-23 | 0.43895 | 0.37725 | 0.27115 | 0.21791 | 0.32586 | 0.39267 | 0.20153
2020-11-24 | 0.65737 | 0.5869 | 0.43772 | 0.40745 | 0.50415 | 0.57762 | 0.31262
2020-11-25 | 0.59145 | 0.53349 | 0.74271 | 0.63184 | 0.40046 | 0.46661 | 0.32173
2020-11-26 | 0.6332 | 0.56467 | 0.06602 | 0.064371 | 0.40317 | 0.46444 | 0.29021
2020-11-27 | 0.63699 | 0.57738 | 0.30646 | 0.31176 | 0.45896 | 0.50835 | 0.29198
2020-11-28 | 0.62919 | 0.56578 | 0.51218 | 0.45461 | 0.48404 | 0.55088 | 0.093523
2020-11-29 | 0.7342 | 0.66955 | 0.73498 | 0.6545 | 0.63913 | 0.71356 | 0.095562
2020-11-30 | 0.79988 | 0.72709 | 0.73078 | 0.64288 | 0.42606 | 0.48397 | 0.2558
2020-12-01 | 0.73051 | 0.67795 | 0.68893 | 0.62808 | 0.053578 | 0.057908 | 0.22505
2020-12-02 | 0.58691 | 0.52311 | 0.68803 | 0.59122 | 0.37537 | 0.42471 | 0.28368
2020-12-03 | 0.75603 | 0.72368 | 0.67511 | 0.60232 | 0.5754 | 0.65018 | 0.30612
2020-12-04 | 0.75564 | 0.69438 | 0.72078 | 0.6325 | 0.57323 | 0.61723 | 0.28606
2020-12-05 | 0.70192 | 0.65794 | 0.72667 | 0.62181 | 0.43615 | 0.46883 | 0.086364
2020-12-06 | 0.66382 | 0.62947 | 0.69531 | 0.63129 | 0.53651 | 0.58175 | 0.082189
2020-12-07 | 0.68362 | 0.63903 | 0.72754 | 0.64146 | 0.51711 | 0.56914 | 0.14696
2020-12-08 | 0.69049 | 0.63857 | 0.696 | 0.65049 | 0.44135 | 0.48329 | 0.24125
2020-12-09 | 0.67589 | 0.62515 | 0.72085 | 0.64966 | 0.44438 | 0.47401 | 0.081234
2020-12-10 | 0.63072 | 0.56168 | 0.68559 | 0.61525 | 0.44229 | 0.46979 | 0.13886
2020-12-11 | 0.70467 | 0.66065 | 0.6742 | 0.66291 | 0.4459 | 0.47642 | 0.082843
2020-12-12 | 0.6582 | 0.60568 | 0.65771 | 0.62626 | 0.43577 | 0.45483 | 0.082316
2020-12-13 | 0.65935 | 0.60721 | 0.628 | 0.61546 | 0.41663 | 0.43812 | 0.084678
2020-12-14 | 0.65651 | 0.61205 | 0.6333 | 0.63545 | 0.43434 | 0.45721 | 0.22239
2020-12-15 | 0.66859 | 0.61953 | 0.46644 | 0.48841 | 0.4269 | 0.44417 | 0.24216
2020-12-16 | 0.7027 | 0.64759 | 0.47346 | 0.46267 | 0.37797 | 0.38211 | 0.29177
2020-12-17 | 0.41525 | 0.37622 | 0.36574 | 0.41535 | 0.42853 | 0.42195 | 0.16548
2020-12-18 | 0.45932 | 0.42496 | 0.050331 | 0.067724 | 0.089692 | 0.089877 | 0.089969
2020-12-19 | 0.40272 | 0.36094 | 0.048422 | 0.065894 | 0.07119 | 0.071745 | 0.99622
2020-12-20 | 0.46113 | 0.42481 | 0.048004 | 0.067031 | 0.072411 | 0.073191 | 1.4108
2020-12-21 | 0.50679 | 0.4589 | 0.2798 | 0.31845 | 0.073631 | 0.073359 | 0.57341
2020-12-22 | 0.54403 | 0.49026 | 0.55067 | 0.56819 | 0.25315 | 0.28026 | 0.42207
2020-12-23 | 0.64007 | 0.58922 | 0.488 | 0.52677 | 0.34844 | 0.41704 | 0.69045
2020-12-24 | 0.68482 | 0.63656 | 0.29021 | 0.32339 | 0.32788 | 0.41842 | 0.75509
2020-12-25 | 0.61482 | 0.56123 | 0.047547 | 0.063984 | 0.075421 | 0.097962 | 0.70341
2020-12-26 | 0.47276 | 0.43249 | 0.040336 | 0.05954 | 0.050366 | 0.070554 | 0.70752
2020-12-27 | 0.45191 | 0.41439 | 0.037813 | 0.057404 | 0.049754 | 0.06414 | 0.69301
2020-12-28 | 0.57351 | 0.52042 | 0.038745 | 0.058539 | 0.029901 | 0.050223 | 0.77384
2020-12-29 | 0.55535 | 0.52948 | 0.42851 | 0.47136 | 0.17579 | 0.21409 | 0.79541
2020-12-30 | 0.67854 | 0.63583 | 0.13377 | 0.12067 | 0.3347 | 0.40019 | 0.70625
2020-12-31 | 0.69417 | 0.64756 | 0.043841 | 0.062335 | 0.33977 | 0.40211 | 0.69108
2021-01-01 | 0.70067 | 0.6726 | 0.044346 | 0.063473 | 0.34857 | 0.41404 | 0.70118
2021-01-02 | 0.67384 | 0.61942 | 0.047309 | 0.064563 | 0.36502 | 0.43043 | 0.70844
2021-01-03 | 0.6765 | 0.62287 | 0.047393 | 0.065616 | 0.3625 | 0.43488 | 0.70197
2021-01-04 | 0.71157 | 0.6532 | 0.047341 | 0.066474 | 0.36225 | 0.445 | 0.69136
2021-01-05 | 0.67838 | 0.66248 | 0.04734 | 0.066587 | 0.20807 | 0.26086 | 0.69757
2021-01-06 | 0.49601 | 0.47084 | 0.050395 | 0.067011 | 0.23616 | 0.28821 | 0.69209
2021-01-07 | 0.68948 | 0.63614 | 0.050755 | 0.067146 | 0.57813 | 0.60732 | 0.63701
2021-01-08 | 0.67138 | 0.62213 | 0.33411 | 0.39322 | 0.59303 | 0.57832 | 0.74039
2021-01-09 | 0.7016 | 0.64938 | 0.35405 | 0.35377 | 0.63991 | 0.62039 | 0.79043
2021-01-10 | 0.70517 | 0.64319 | 0.048391 | 0.067703 | 0.64264 | 0.61196 | 0.69077
2021-01-11 | 0.71149 | 0.6456 | 0.16795 | 0.17254 | 0.63962 | 0.60487 | 0.70012
2021-01-12 | 0.73802 | 0.69287 | 0.04999 | 0.069498 | 0.66504 | 0.61446 | 0.79225
2021-01-13 | 0.75077 | 0.68412 | 0.048524 | 0.068778 | 0.64408 | 0.60148 | 0.72336
2021-01-14 | 0.67522 | 0.60801 | 0.052159 | 0.071949 | 0.58877 | 0.54592 | 0.75551
2021-01-15 | 0.72053 | 0.66181 | 0.29871 | 0.37834 | 0.63561 | 0.59044 | 0.72582
2021-01-16 | 0.73906 | 0.67311 | 0.37521 | 0.41877 | 0.66187 | 0.61304 | 0.67712
2021-01-17 | 0.65902 | 0.62949 | 0.47856 | 0.55353 | 0.42792 | 0.39706 | 0.36224
2021-01-18 | 0.73995 | 0.68837 | 0.39355 | 0.42659 | 0.27175 | 0.25241 | 0.53545
2021-01-19 | 0.73881 | 0.68647 | 0.42339 | 0.48087 | 0.72243 | 0.67772 | 0.79142
2021-01-20 | 0.65846 | 0.60081 | 0.49912 | 0.57964 | 0.4742 | 0.4457 | 0.71535
2021-01-21 | 0.65078 | 0.62624 | 0.34721 | 0.3493 | 0.71585 | 0.67578 | 0.62671
2021-01-22 | 0.28632 | 0.37277 | 0.32284 | 0.40682 | 0.72653 | 0.66798 | 0.68415
2021-01-23 | 0.27353 | 0.35941 | 0.48321 | 0.51494 | 0.56603 | 0.52833 | 0.67944
2021-01-24 | 0.21865 | 0.22925 | 0.22199 | 0.28121 | 0.39944 | 0.37207 | 0.68144
2021-01-25 | 0.18761 | 0.19158 | 0.33903 | 0.4095 | 0.40795 | 0.37998 | 0.7124
2021-01-26 | 0.57013 | 0.6746 | 0.46052 | 0.53727 | 0.4402 | 0.40964 | 0.75511
2021-01-27 | 0.72632 | 0.81914 | 0.47061 | 0.53646 | 0.4537 | 0.42527 | 0.74045
2021-01-28 | 0.51206 | 0.54658 | 0.49865 | 0.5791 | 0.31258 | 0.29967 | 0.67667
2021-01-29 | 0.67576 | 0.70564 | 0.51087 | 0.5871 | 0.4194 | 0.40893 | 0.73918
2021-01-30 | 0.65769 | 0.6936 | 0.51922 | 0.58223 | 0.41774 | 0.40399 | 0.60102
2021-01-31 | 0.7951 | 0.92086 | 0.51182 | 0.58115 | 0.47608 | 0.44586 | 0.74079
2021-02-01 | 0.78075 | 0.88079 | 0.46961 | 0.5328 | 0.45892 | 0.43072 | 0.58141
2021-02-02 | 0.41692 | 0.86508 | 0.24804 | 0.25243 | 0.45563 | 0.42977 | 0.72526
2021-02-03 | 0.4019 | 0.51298 | 0.14671 | 0.12682 | 0.51883 | 0.49354 | 0.78642
2021-02-04 | 0.45646 | 0.42717 | 0.066454 | 0.071026 | 0.50998 | 0.48519 | 0.71501
2021-02-05 | 0.71271 | 0.62523 | 0.064093 | 0.070144 | 0.56205 | 0.54703 | 0.64191
2021-02-06 | 0.75136 | 0.72382 | 0.061899 | 0.068678 | 0.57134 | 0.55522 | 0.68594
2021-02-07 | 0.73597 | 0.75581 | 0.062878 | 0.069467 | 0.58878 | 0.56432 | 0.68408
2021-02-08 | 0.74574 | 0.76033 | 0.062339 | 0.068908 | 0.62035 | 0.58863 | 0.73805
2021-02-09 | 0.74951 | 0.70654 | 0.06145 | 0.070623 | 0.42878 | 0.41604 | 0.75605
2021-02-10 | 0.6281 | 0.69199 | 0.056652 | 0.068281 | 0.077576 | 0.077305 | 0.72199
2021-02-11 | 0.66935 | 0.65986 | 0.050845 | 0.064745 | 0.074645 | 0.074786 | 0.72246
2021-02-12 | 0.60404 | 0.65989 | 0.16704 | 0.17629 | 0.069858 | 0.071511 | 0.68954
2021-02-13 | 0.65742 | 0.65112 | 0.63979 | 0.53778 | 0.073781 | 0.074786 | 0.7027
2021-02-14 | 0.68227 | 0.72149 | 0.67093 | 0.59854 | 0.074713 | 0.074786 | 0.69123
2021-02-15 | 0.68705 | 0.69826 | 0.6733 | 0.56786 | 0.074688 | 0.074786 | 0.80834
2021-02-16 | 0.59481 | 0.44649 | 0.7043 | 0.6073 | 0.064809 | 0.071018 | 0.83676
2021-02-17 | 0.61116 | 0.6975 | 0.3232 | 0.25949 | 0.054954 | 0.060584 | 0.085839
2021-02-18 | 0.53952 | 0.45966 | 0.40299 | 0.35856 | 0.051675 | 0.053804 | 0.46253
2021-02-19 | 0.55757 | 0.39218 | 0.49008 | 0.38981 | 0.055144 | 0.060517 | 0.087115
2021-02-20 | 0.60513 | 0.67571 | 0.061967 | 0.061799 | 0.060074 | 0.068923 | 0.083749
2021-02-21 | 0.60881 | 0.53606 | 0.061021 | 0.062956 | 0.054135 | 0.063216 | 0.081189
2021-02-22 | 0.61944 | 0.51622 | 0.063054 | 0.064374 | 0.066879 | 0.082159 | 0.080608
2021-02-23 | 0.59025 | 0.68187 | 0.065817 | 0.064921 | 0.075616 | 0.082106 | 0.097307
2021-02-24 | 0.67389 | 0.63515 | 0.066287 | 0.065723 | 0.07529 | 0.079687 | 0.08146
2021-02-25 | 0.67978 | 0.74844 | 0.066338 | 0.066571 | 0.067395 | 0.073406 | 0.35427
2021-02-26 | 0.6678 | 0.78185 | 0.066362 | 0.066475 | 0.065934 | 0.081246 | 0.37868
2021-02-27 | 0.69947 | 0.67616 | 0.067039 | 0.065821 | 0.076228 | 0.088769 | 0.14452
2021-02-28 | 0.70258 | 0.69907 | 0.067267 | 0.066608 | 0.073982 | 0.077781 | 0.082662
2021-03-01 | 0.72881 | 0.69291 | 0.06641 | 0.067055 | 0.074097 | 0.078751 | 0.46752
2021-03-02 | 0.69812 | 0.56873 | 0.066567 | 0.066614 | 0.074786 | 0.076886 | 0.68408
2021-03-03 | 0.49867 | 0.51814 | 0.066743 | 0.067031 | 0.074786 | 0.074967 | 0.64474
2021-03-04 | 0.65155 | 0.62682 | 0.075498 | 0.089992 | 0.073633 | 0.074786 | 0.77831
2021-03-05 | 0.69938 | 0.76483 | 0.067309 | 0.068338 | 0.074481 | 0.075833 | 0.85138
2021-03-06 | 0.72268 | 0.82926 | 0.067188 | 0.067343 | 0.064129 | 0.074786 | 0.901
2021-03-07 | 0.72534 | 0.68993 | 0.064494 | 0.063084 | 0.065364 | 0.074786 | 0.67093
2021-03-08 | 0.68673 | 0.73201 | 0.057608 | 0.059363 | 0.066632 | 0.074786 | 0.69457
2021-03-09 | 0.69997 | 0.768 | 0.06222 | 0.062749 | 0.065797 | 0.062216 | 0.7124
2021-03-10 | 0.70865 | 0.62541 | 0.066212 | 0.064564 | 0.058631 | 0.041016 | 0.79982
2021-03-11 | 0.60694 | 0.63264 | 0.066875 | 0.066794 | 0.045508 | 0.039465 | 0.88769
2021-03-12 | 0.65363 | 0.66452 | 0.066022 | 0.063402 | 0.024386 | 0.02442 | 0.72977
2021-03-13 | 0.7101 | 0.71305 | 0.051615 | 0.053904 | 0.025714 | 0.024777 | 0.67263
2021-03-14 | 0.72937 | 0.80554 | 0.050598 | 0.055079 | 0.03528 | 0.02966 | 0.12712
2021-03-15 | 0.53451 | 0.61922 | 0.056751 | 0.05956 | 0.040342 | 0.034786 | 0.54067
2021-03-16 | 0.28828 | 0.34725 | 0.07164 | 0.072798 | 0.045357 | 0.044538 | 0.67518
2021-03-17 | 0.42147 | 0.49392 | 0.055276 | 0.05935 | 0.047291 | 0.050218 | 0.68608
2021-03-18 | 0.47597 | 0.56181 | 0.050958 | 0.054333 | 0.050366 | 0.050366 | 0.55655
2021-03-19 | 0.67473 | 0.74404 | 0.052114 | 0.056404 | 0.050366 | 0.050366 | 0.75172
2021-03-20 | 0.093042 | 0.10251 | 0.055312 | 0.059104 | 0.050366 | 0.050366 | 0.78128
2021-03-21 | 0.09163 | 0.10431 | 0.058684 | 0.061562 | 0.051483 | 0.058184 | 0.75157
2021-03-22 | 0.26984 | 0.34462 | 0.062398 | 0.063444 | 0.05685 | 0.072889 | 0.76701
2021-03-23 | 0.51566 | 0.58607 | 0.06036 | 0.10936 | 0.060734 | 0.077804 | 0.6271
2021-03-24 | 0.70112 | 0.69875 | 0.057437 | 0.068362 | 0.06496 | 0.078023 | 0.52616
2021-03-25 | 0.45243 | 0.31982 | 0.12201 | 0.078055 | 0.064738 | 0.074786 | 0.094247
2021-03-26 | 0.30171 | 0.45743 | 0.069853 | 0.065104 | 0.065691 | 0.080342 | 0.085062
2021-03-27 | 0.073672 | 0.080755 | 0.071086 | 0.064804 | 0.067615 | 0.078662 | 0.085083
2021-03-28 | 0.078253 | 0.081354 | 0.07469 | 0.066307 | 0.061734 | 0.074859 | 0.086482
2021-03-29 | 0.51903 | 0.54436 | 0.46197 | 0.37315 | 0.056426 | 0.074786 | 0.53405
2021-03-30 | 0.71462 | 0.79374 | 0.64939 | 0.50003 | 0.059656 | 0.083028 | 0.27413
2021-03-31 | 0.75869 | 0.81456 | 0.76639 | 0.59306 | 0.0693 | 0.078731 | 0.53787
2021-04-01 | 0.75792 | 0.79954 | 0.78434 | 0.6192 | 0.063193 | 0.074786 | 0.74261
2021-04-02 | 0.76257 | 0.74373 | 0.79656 | 0.61644 | 0.061073 | 0.074786 | 0.77296
2021-04-03 | 0.7644 | 0.82644 | 0.77799 | 0.59277 | 0.067637 | 0.074786 | 0.74927
2021-04-04 | 0.82447 | 0.88602 | 0.86383 | 0.6645 | 0.079254 | 0.089816 | 0.21871
2021-04-04 23:00 | 0.76008 | 0.77458 | 0.78549 | 0.60599 | 0.074786 | 0.096998 | 0.083208
2021-04-05 23:00 | 0.76268 | 0.82879 | 0.77615 | 0.5845 | 0.074786 | 0.093631 | 0.53321
2021-04-06 23:00 | 0.76816 | 0.81413 | 0.24462 | 0.17132 | 0.07428 | 0.097431 | 0.82997
2021-04-07 23:00 | 0.77472 | 0.82785 | 0.45752 | 0.37198 | 0.074712 | 0.097093 | 0.67237
2021-04-08 23:00 | 0.77393 | 0.80226 | 0.67428 | 0.49164 | 0.074314 | 0.098241 | 0.37912
2021-04-09 23:00 | 0.76379 | 0.80157 | 0.79714 | 0.58749 | 0.072176 | 0.092497 | 0.085582
2021-04-10 23:00 | 0.77422 | 0.80801 | 0.79431 | 0.58082 | 0.068102 | 0.089836 | 0.08541
2021-04-11 23:00 | 0.76454 | 0.82355 | 0.74898 | 0.55298 | 0.049351 | 0.070009 | 0.52612
2021-04-12 23:00 | 0.71076 | 0.74456 | 0.75098 | 0.54542 | 0.032693 | 0.050371 | 0.65672
2021-04-13 23:00 | 0.55563 | 0.57408 | 0.57391 | 0.43921 | 0.025958 | 0.044658 | 0.5248
2021-04-14 23:00 | 0.6449 | 0.62248 | 0.55351 | 0.41157 | 0.02442 | 0.031249 | 0.75926
2021-04-15 23:00 | 0.60913 | 0.58573 | 0.73551 | 0.54163 | 0.02457 | 0.031543 | 0.78289
2021-04-16 23:00 | 0.63377 | 0.64398 | 0.78403 | 0.58424 | 0.024601 | 0.033668 | 0.87468
2021-04-17 23:00 | 0.65495 | 0.67193 | 0.80555 | 0.60076 | 0.02442 | 0.029327 | 0.29379
2021-04-18 23:00 | 0.32416 | 0.32825 | 0.77808 | 0.54121 | 0.024456 | 0.029067 | 0.57904
2021-04-19 23:00 | 0.44454 | 0.40941 | 0.43102 | 0.13675 | 0.02442 | 0.031086 | 0.76372
2021-04-20 23:00 | 0.72472 | 0.74514 | 0.08484 | 0.067538 | 0.034791 | 0.047405 | 0.76862
2021-04-21 23:00 | 0.72171 | 0.73797 | 0.078772 | 0.066291 | 0.034185 | 0.048065 | 0.78707
2021-04-22 23:00 | 0.72615 | 0.75807 | 0.080786 | 0.068732 | 0.029284 | 0.04225 | 0.80395
2021-04-23 23:00 | 0.7195 | 0.74428 | 0.084153 | 0.07034 | 0.036169 | 0.050366 | 0.78472
2021-04-24 23:00 | 0.71694 | 0.73411 | 0.08403 | 0.070388 | 0.038616 | 0.050366 | 0.79683
2021-04-25 23:00 | 0.71135 | 0.71488 | 0.084386 | 0.068321 | 0.044204 | 0.050366 | 0.78844
2021-04-26 23:00 | 0.39896 | 0.3996 | 0.083007 | 0.067689 | 0.04914 | 0.050366 | 0.79113
2021-04-27 23:00 | 0.095126 | 0.092196 | 0.07656 | 0.066088 | 0.042077 | 0.049678 | 0.78194
2021-04-28 23:00 | 0.095247 | 0.090652 | 0.075664 | 0.06493 | 0.032956 | 0.049466 | 0.77069
2021-04-29 23:00 | 0.46184 | 0.47119 | 0.078484 | 0.066317 | 0.044297 | 0.050258 | 0.77611
2021-04-30 23:00 | 0.77844 | 0.80116 | 0.081552 | 0.068189 | 0.044691 | 0.050366 | 0.75016
2021-05-01 23:00 | 0.79445 | 0.82083 | 0.083295 | 0.070014 | 0.046254 | 0.050366 | 0.72879
2021-05-02 23:00 | 0.80429 | 0.83398 | 0.083333 | 0.069981 | 0.050255 | 0.052357 | 0.7915
2021-05-03 23:00 | 0.80958 | 0.83121 | 0.27705 | 0.18304 | 0.050366 | 0.057444 | 0.76674
2021-05-04 23:00 | 0.39361 | 0.39456 | 0.50379 | 0.3349 | 0.050366 | 0.057867 | 0.76402
2021-05-05 23:00 | 0.092822 | 0.088658 | 0.80958 | 0.50516 | 0.049987 | 0.050638 | 0.78586
2021-05-06 23:00 | 0.094142 | 0.085679 | 0.70735 | 0.496 | 0.049631 | 0.050366 | 0.86873
2021-05-07 23:00 | 0.097006 | 0.088602 | 0.66986 | 0.55995 | 0.050197 | 0.050923 | 0.84346
2021-05-08 23:00 | 0.097203 | 0.091539 | 0.19543 | 0.14761 | 0.050366 | 0.051008 | 0.79245
2021-05-09 23:00 | 0.096189 | 0.091002 | 0.34084 | 0.32895 | 0.040664 | 0.040072 | 0.78517
2021-05-10 23:00 | 0.092428 | 0.08771 | 0.6864 | 0.58245 | 0.24633 | 0.27184 | 0.77074
2021-05-11 23:00 | 0.16835 | 0.16312 | 0.70463 | 0.60523 | 0.50285 | 0.58743 | 0.78516
2021-05-12 23:00 | 0.11134 | 0.10508 | 0.69111 | 0.58045 | 0.50861 | 0.60435 | 0.84711
2021-05-13 23:00 | 0.32002 | 0.32074 | 0.5629 | 0.46719 | 0.53699 | 0.63432 | 0.83005
2021-05-14 23:00 | 0.35366 | 0.34915 | 0.5921 | 0.50473 | 0.52334 | 0.63858 | 0.78302
2021-05-15 23:00 | 0.34204 | 0.35147 | 0.34288 | 0.27764 | 0.51115 | 0.63637 | 0.75675
2021-05-16 23:00 | 0.28021 | 0.27237 | 0.38641 | 0.3671 | 0.58941 | 0.64111 | 0.75696
2021-05-17 23:00 | 0.25056 | 0.25194 | 0.70008 | 0.59419 | 0.76744 | 0.72407 | 0.80592
2021-05-18 23:00 | 0.22225 | 0.21324 | 0.67214 | 0.55654 | 0.64839 | 0.60165 | 0.80115
2021-05-19 23:00 | 0.51308 | 0.53079 | 0.57301 | 0.47404 | 0.85779 | 0.80684 | 0.74202
2021-05-20 23:00 | 0.69453 | 0.69822 | 0.4842 | 0.41997 | 0.85173 | 0.79088 | 0.78728
2021-05-21 23:00 | 0.75956 | 0.7647 | 0.61769 | 0.52446 | 0.83295 | 0.77274 | 0.7827
2021-05-22 23:00 | 0.7241 | 0.74128 | 0.63016 | 0.54303 | 0.72791 | 0.67645 | 0.77828
2021-05-23 23:00 | 0.53041 | 0.57393 | 0.57099 | 0.44092 | 0.6631 | 0.6127 | 0.67844
2021-05-24 23:00 | 0.50042 | 0.3007 | 0.051667 | 0.058675 | 0.54521 | 0.5204 | 0.78976
2021-05-25 23:00 | 0.68423 | 0.76246 | 0.04369 | 0.055574 | 0.52921 | 0.5933 | 0.75503
2021-05-26 23:00 | 0.69819 | 0.66638 | 0.043232 | 0.055641 | 0.43385 | 0.61893 | 0.54158
2021-05-27 23:00 | 0.71365 | 0.68035 | 0.04753 | 0.057041 | 0.54771 | 0.64418 | 0.75285
2021-05-28 23:00 | 0.72277 | 0.72727 | 0.052553 | 0.060583 | 0.61192 | 0.64961 | 0.75534
2021-05-29 23:00 | 0.71885 | 0.7329 | 0.055613 | 0.062964 | 0.60277 | 0.64729 | 0.76475
2021-05-30 23:00 | 0.69836 | 0.70733 | 0.057868 | 0.063559 | 0.58008 | 0.62295 | 0.76028
2021-05-31 23:00 | 0.66962 | 0.67968 | 0.056855 | 0.063112 | 0.57829 | 0.61276 | 0.75589
2021-06-01 23:00 | 0.68908 | 0.70286 | 0.051912 | 0.058588 | 0.64377 | 0.70397 | 0.77142
2021-06-02 23:00 | 0.72534 | 0.74148 | 0.046637 | 0.056574 | 0.64891 | 0.66518 | 0.83546
2021-06-03 23:00 | 0.70782 | 0.63253 | 0.048826 | 0.058848 | 0.57276 | 0.5611 | 0.75981
2021-06-04 23:00 | 0.6995 | 0.71672 | 0.053824 | 0.060825 | 0.55183 | 0.55501 | 0.75893
2021-06-05 23:00 | 0.69489 | 0.71346 | 0.056698 | 0.062196 | 0.54964 | 0.55914 | 0.74847
2021-06-06 23:00 | 0.70189 | 0.73024 | 0.05871 | 0.064164 | 0.57117 | 0.58238 | 0.75447
2021-06-07 23:00 | 0.48835 | 0.50331 | 0.060147 | 0.065911 | 0.59077 | 0.61474 | 0.75962
2021-06-08 23:00 | 0.24552 | 0.24241 | 0.064384 | 0.067823 | 0.50566 | 0.51546 | 0.74718
2021-06-09 23:00 | 0.10134 | 0.097226 | 0.063202 | 0.066777 | 0.084794 | 0.06859 | 0.75357
2021-06-10 23:00 | 0.12785 | 0.11764 | 0.065243 | 0.068099 | 0.33081 | 0.33789 | 0.74745
2021-06-11 23:00 | 0.2175 | 0.21292 | 0.06536 | 0.068099 | 0.44415 | 0.46275 | 0.73477
2021-06-12 23:00 | 0.22656 | 0.23208 | 0.06636 | 0.06805 | 0.43851 | 0.46254 | 0.73531
2021-06-13 23:00 | 0.18202 | 0.18391 | 0.067772 | 0.068235 | 0.29531 | 0.30757 | 0.75028
2021-06-14 23:00 | 0.09738 | 0.095477 | 0.067295 | 0.067494 | 0.41457 | 0.43527 | 0.73916
2021-06-15 23:00 | 0.16639 | 0.16138 | 0.061742 | 0.063805 | 0.41605 | 0.44078 | 0.76833
2021-06-16 23:00 | 0.22603 | 0.23231 | 0.058865 | 0.061815 | 0.57263 | 0.6151 | 0.7861
2021-06-17 23:00 | 0.24398 | 0.29656 | 0.063698 | 0.20015 | 0.69375 | 0.75384 | 0.76455
2021-06-18 23:00 | 0.24537 | 0.13683 | 0.0416 | 0.12891 | 0.64926 | 0.70399 | 0.75584
2021-06-19 23:00 | 0.10315 | 0.056326 | 0.04589 | 0.11701 | 0.54893 | 0.59226 | 0.75387
2021-06-20 23:00 | 0.093644 | 0.045427 | 0.047697 | 0.10365 | 0.74271 | 0.80954 | 0.77518
2021-06-21 23:00 | 0.1108 | 0.057892 | 0.048903 | 0.066541 | 0.54076 | 0.5909 | 0.72637
2021-06-22 23:00 | 0.17688 | 0.10341 | 0.041531 | 0.059758 | 0.48549 | 0.52837 | 0.74102
2021-06-23 23:00 | 0.20568 | 0.12473 | 0.039884 | 0.060007 | 0.50693 | 0.56223 | 0.80114
2021-06-24 23:00 | 0.18524 | 0.15424 | 0.041813 | 0.059519 | 0.54507 | 0.60987 | 0.75534
2021-06-25 23:00 | 0.22009 | 0.19804 | 0.046738 | 0.060564 | 0.58103 | 0.65885 | 0.73285
2021-06-26 23:00 | 0.22231 | 0.19075 | 0.046927 | 0.06165 | 0.57283 | 0.65955 | 0.42232
2021-06-27 23:00 | 0.15418 | 0.13261 | 0.047679 | 0.061976 | 0.44233 | 0.49105 | 0.42748
2021-06-28 23:00 | 0.094841 | 0.07656 | 0.042177 | 0.059279 | 0.065843 | 0.41725 | 0.74118
2021-06-29 23:00 | 0.095486 | 0.07761 | 0.038692 | 0.056042 | 3.1877 | 0.17829 | 0.73727
2021-06-30 23:00 | 0.092892 | 0.073945 | 0.034128 | 0.053658 | 0 | 0.2232 | 0.52282

## 21-22
Date Stamp | .Gear Island 1050 Fluoride | .Gear Island 1050 Fluoride Analyser #2 | .Te Marua PS Fluoride Residual | .Te Marua TP Fluoride Residual | .Wainui Fluoride Building Fluoride Residual Stream 1 | .Wainui Fluoride Building Fluoride Residual Stream 2 | .Waterloo Naenae Fluoride Residual
2021-07-01 23:00 | 0.089157 | 0.072247 | 0.034007 | 0.053798 | 0 | 0.12193 | 0.3255
2021-07-02 23:00 | 0.091631 | 0.072516 | 0.037172 | 0.056607 | 0 | 0.18847 | 0.46424
2021-07-03 23:00 | 0.086609 | 0.068834 | 0.039818 | 0.059385 | 0.11083 | 0.17292 | 0.08733
2021-07-04 23:00 | 0.091827 | 0.073185 | 0.042827 | 0.060867 | 0.0007855 | 0.10993 | 0.48112 |  | Fluoride not dosed
2021-07-05 23:00 | 0.094031 | 0.0755 | 0.048538 | 0.064868 | 0 | 0.14309 | 0.69889 |  | fluoride dosed but outside recommended range
2021-07-06 23:00 | 0.094388 | 0.078142 | 0.052773 | 0.064691 | 0 | 0.5032 | 0.78787 |  | Fluoride dosed but within recommended range
2021-07-07 23:00 | 0.096893 | 0.07871 | 0.050439 | 0.064817 | 0.048799 | 1.1563 | 0.81449
2021-07-08 23:00 | 0.087222 | 0.071617 | 0.046031 | 0.065102 | 0.035879 | 0.33211 | 0.73733 | Assumptions: |  | 1. Values less than 0.1 indicates that fluoride is not being dosed
2021-07-09 23:00 | 0.08867 | 0.071482 | 0.045933 | 0.065079 | 0.024403 | 0.1528 | 0.69482 |  |  | 2. MAV exceedences are due to the default value that the analyser goes to when fluoride dosing is ceased
2021-07-10 23:00 | 0.091797 | 0.075656 | 0.047513 | 0.065237 | 0.011713 | 0.16979 | 0.75884 |  |  | 3. The Gear Island sampling point is downstream of the plant and can contain a residual from the Wainuiomata WTP
2021-07-11 23:00 | 0.091792 | 0.074964 | 0.04753 | 0.065294 | 0.17974 | 0.16209 | 0.80311 |  |  | 4. Gear Island fluoride dosing was turned off on the 24/11/21
2021-07-12 23:00 | 0.090833 | 0.071674 | 0.042339 | 0.065263 | 0.24676 | 0.21446 | 0.81116
2021-07-13 23:00 | 0.095772 | 0.080341 | 2.3661 | 0.065329 | 0.28951 | 0.35477 | 0.57445
2021-07-14 23:00 | 0.17077 | 0.14929 | 4.9874 | 0.064925 | 0.63932 | 0.70698 | 0.19099
2021-07-15 23:00 | 0.25952 | 0.22685 | 4.9879 | 0.064718 | 0.74827 | 0.77337 | 0.34915
2021-07-16 23:00 | 0.24797 | 0.22137 | 4.988 | 0.064564 | 0.70925 | 0.73955 | 0.49412
2021-07-17 23:00 | 0.091535 | 0.072606 | 4.9883 | 0.064486 | 0.68005 | 0.72351 | 0.47207
2021-07-18 23:00 | 0.10489 | 0.089359 | 4.9882 | 0.064641 | 0.67195 | 0.74246 | 0.52577
2021-07-19 23:00 | 0.22285 | 0.19819 | 4.988 | 0.064809 | 0.68163 | 0.8361 | 0.34171
2021-07-20 23:00 | 0.24423 | 0.22514 | 4.9879 | 0.064677 | 0.70373 | 0.80171 | 0.30661
2021-07-21 23:00 | 0.19855 | 0.17603 | 4.988 | 0.064622 | 0.58104 | 0.58242 | 0.23111
2021-07-22 23:00 | 0.099509 | 0.084798 | 4.9881 | 0.064711 | 0.31259 | 0.30861 | 0.4725
2021-07-23 23:00 | 0.19928 | 0.20854 | 4.9876 | 0.064994 | 0.29251 | 0.2864 | 0.71585
2021-07-24 23:00 | 0.0884 | 0.069122 | 4.9876 | 0.065003 | 0.28378 | 0.2737 | 0.72003
2021-07-25 23:00 | 0.23142 | 0.20507 | 4.9878 | 0.06483 | 0.78729 | 0.7834 | 0.69808
2021-07-26 23:00 | 0.24032 | 0.20899 | 4.9879 | 0.064715 | 0.8072 | 0.79696 | 0.70836
2021-07-27 23:00 | 0.27479 | 0.24462 | 4.9877 | 0.064916 | 0.82363 | 0.81573 | 0.72231
2021-07-28 23:00 | 0.27932 | 0.24675 | 4.9875 | 0.064995 | 0.84524 | 0.83486 | 0.73147
2021-07-29 23:00 | 0.37289 | 0.34806 | 4.9877 | 0.064807 | 0.86361 | 0.84953 | 0.74219
2021-07-30 23:00 | 0.35469 | 0.33067 | 4.9877 | 0.064749 | 0.87671 | 0.85585 | 0.73945
2021-07-31 23:00 | 0.35177 | 0.32015 | 4.9873 | 0.064725 | 0.88117 | 0.8595 | 0.73962
2021-08-01 23:00 | 0.37483 | 0.3447 | 4.9876 | 0.064829 | 0.88273 | 0.85937 | 0.73028
2021-08-02 23:00 | 0.34926 | 0.32502 | 4.9875 | 0.064846 | 0.81745 | 0.7858 | 0.74587
2021-08-03 23:00 | 0.19917 | 0.17272 | 4.9873 | 0.065019 | 0.56922 | 0.54423 | 0.74217
2021-08-04 23:00 | 0.23134 | 0.20512 | 4.9873 | 0.067359 | 0.64915 | 0.62565 | 0.74073
2021-08-05 23:00 | 0.29674 | 0.27034 | 4.9874 | 0.07363 | 0.76406 | 0.73973 | 0.7556
2021-08-06 23:00 | 0.31319 | 0.28537 | 4.9875 | 0.06337 | 0.8319 | 0.80672 | 0.77715
2021-08-07 23:00 | 0.31198 | 0.28799 | 4.9876 | 0.058169 | 0.86057 | 0.82069 | 0.78817
2021-08-08 23:00 | 0.2335 | 0.21109 | 4.9876 | 0.060908 | 0.80659 | 0.75963 | 0.75296
2021-08-09 23:00 | 0.26139 | 0.25515 | 4.9872 | 0.050701 | 0.65482 | 0.61012 | 0.78893
2021-08-10 23:00 | 0.14758 | 0.13598 | 4.987 | 0.047901 | 0.39176 | 0.37876 | 0.7634
2021-08-11 23:00 | 0.22332 | 0.21542 | 4.9871 | 0.04885 | 0.42369 | 0.41838 | 0.80428
2021-08-12 23:00 | 0.32325 | 0.32746 | 4.9874 | 0.051441 | 0.57387 | 0.5712 | 0.8124
2021-08-13 23:00 | 0.34673 | 0.35293 | 4.9875 | 0.050075 | 0.66713 | 0.66633 | 0.8064
2021-08-14 23:00 | 0.35558 | 0.36 | 4.9874 | 0.049958 | 0.68887 | 0.68373 | 0.12084
2021-08-15 23:00 | 0.37365 | 0.37138 | 4.9876 | 0.052429 | 0.70595 | 0.70194 | 0.48502
2021-08-16 23:00 | 0.34767 | 0.36026 | 4.9879 | 0.055401 | 0.665 | 0.66546 | 0.80804
2021-08-17 23:00 | 0.31549 | 0.3506 | 4.988 | 0.054501 | 0.64766 | 0.64427 | 0.81172
2021-08-18 23:00 | 0.32181 | 0.34482 | 4.9877 | 0.052154 | 0.67747 | 0.67033 | 0.80822
2021-08-19 23:00 | 0.20991 | 0.21761 | 4.9876 | 0.052728 | 0.45433 | 0.44557 | 0.80147
2021-08-20 23:00 | 0.31694 | 0.3339 | 4.9873 | 0.053714 | 0.68963 | 0.68677 | 0.80771
2021-08-21 23:00 | 0.32335 | 0.35167 | 4.9872 | 0.054448 | 0.66975 | 0.66669 | 0.80958
2021-08-22 23:00 | 0.32746 | 0.35812 | 4.9875 | 0.05694 | 0.69426 | 0.69751 | 0.79883
2021-08-23 23:00 | 0.29954 | 0.32886 | 4.9876 | 0.058103 | 0.73083 | 0.73319 | 0.81052
2021-08-24 23:00 | 0.3098 | 0.31071 | 4.9878 | 0.059506 | 0.7634 | 0.76876 | 0.8122
2021-08-25 23:00 | 0.25757 | 0.26784 | 4.9879 | 0.060395 | 0.55738 | 0.55637 | 0.80202
2021-08-26 23:00 | 0.42285 | 0.47657 | 4.9859 | 0.061546 | 0.78174 | 0.78494 | 0.81117
2021-08-27 23:00 | 0.37246 | 0.39309 | 4.9881 | 0.059276 | 0.76069 | 0.76749 | 0.81992
2021-08-28 23:00 | 0.33317 | 0.36746 | 4.9879 | 0.053044 | 0.73481 | 0.74429 | 0.81278
2021-08-29 23:00 | 0.27303 | 0.27721 | 4.9878 | 0.05212 | 0.53858 | 0.52464 | 0.81758
2021-08-30 23:00 | 0.37915 | 0.45886 | 4.9874 | 0.051554 | 0.8292 | 0.80945 | 0.80839
2021-08-31 23:00 | 0.38238 | 0.28882 | 4.9872 | 0.052192 | 0.82608 | 0.80603 | 0.36332
2021-09-01 23:00 | 0.40166 | 0.38928 | 4.9871 | 0.053639 | 0.82907 | 0.80399 | 0.08759
2021-09-02 23:00 | 0.37791 | 0.36792 | 4.9872 | 0.055902 | 0.83441 | 0.80379 | 0.46511
2021-09-03 23:00 | 0.41951 | 0.40388 | 4.9872 | 0.057946 | 0.84292 | 0.80869 | 0.33032
2021-09-04 23:00 | 0.42478 | 0.42537 | 4.9874 | 0.06019 | 0.83521 | 0.79823 | 0.81532
2021-09-05 23:00 | 0.41716 | 0.40797 | 4.9876 | 0.060332 | 0.83684 | 0.79955 | 0.78698
2021-09-06 23:00 | 0.40349 | 0.39766 | 4.9878 | 0.060977 | 0.83412 | 0.79833 | 0.81781
2021-09-07 23:00 | 0.41095 | 0.40718 | 4.9877 | 0.059426 | 0.84264 | 0.80905 | 0.52576
2021-09-08 23:00 | 0.36185 | 0.34273 | 4.9876 | 0.055905 | 0.84816 | 0.80288 | 0.78661
2021-09-09 23:00 | 0.37898 | 0.38083 | 4.9877 | 0.054199 | 0.83859 | 0.79413 | 0.84096
2021-09-10 23:00 | 0.28725 | 0.27585 | 4.9877 | 0.052675 | 0.81792 | 0.77478 | 0.10934
2021-09-11 23:00 | 0.2747 | 0.27475 | 4.9876 | 0.050605 | 0.81255 | 0.78265 | 0.11309
2021-09-12 23:00 | 0.27123 | 0.26561 | 4.9878 | 0.053191 | 0.76424 | 0.73117 | 0.11866
2021-09-13 23:00 | 0.12006 | 0.1125 | 4.9879 | 0.053097 | 0.28048 | 0.27022 | 0.10671
2021-09-14 23:00 | 0.3035 | 0.30345 | 4.9875 | 0.049336 | 0.72485 | 0.71437 | 0.087541
2021-09-15 23:00 | 0.37087 | 0.4572 | 4.9876 | 0.050681 | 0.8131 | 0.79812 | 0.091741
2021-09-16 23:00 | 0.38003 | 0.33194 | 4.9874 | 0.050113 | 0.81622 | 0.79612 | 0.11419
2021-09-17 23:00 | 0.38568 | 0.28814 | 4.9873 | 0.050188 | 0.81431 | 0.80308 | 0.087371
2021-09-18 23:00 | 0.42395 | 0.40875 | 4.9873 | 0.051823 | 0.8224 | 0.81031 | 0.09017
2021-09-19 23:00 | 0.38217 | 0.3758 | 4.9875 | 0.0552 | 0.81445 | 0.79933 | 0.20265
2021-09-20 23:00 | 0.35754 | 0.35048 | 4.9877 | 0.056322 | 0.80864 | 0.79223 | 0.29692
2021-09-21 23:00 | 0.36211 | 0.35431 | 4.9878 | 0.05397 | 0.485 | 0.47041 | 0.32787
2021-09-22 23:00 | 0.095186 | 0.087789 | 4.9881 | 0.053504 | 0.050434 | 0.050255 | 0.27011
2021-09-23 23:00 | 0.16544 | 0.15489 | 4.988 | 0.086203 | 0.52114 | 0.48856 | 0.67168
2021-09-24 23:00 | 0.41706 | 0.40807 | 4.9881 | 0 | 0.80946 | 0.77806 | 0.39915
2021-09-25 23:00 | 0.38714 | 0.39585 | 4.988 | 0 | 0.82321 | 0.78235 | 0.087927
2021-09-27 | 0.39941 | 0.40404 | 4.9878 | 0.13166 | 0.81304 | 0.77788 | 0.50803
2021-09-28 | 0.34801 | 0.34266 | 4.9876 | 0.047757 | 0.58192 | 0.5557 | 0.70425
2021-09-29 | 0.14657 | 0.14316 | 4.9875 | 0.048322 | 0.47454 | 0.48326 | 0.33008
2021-09-30 | 0.33016 | 0.3356 | 4.9878 | 0.051809 | 0.76739 | 0.77378 | 0.54217
2021-10-01 | 0.30877 | 0.30329 | 4.9876 | 0.052523 | 0.70209 | 0.737 | 0.49097
2021-10-02 | 0.36214 | 0.36188 | 4.9878 | 0.055556 | 0.69755 | 0.70946 | 0.19288
2021-10-03 | 0.35915 | 0.36661 | 4.9881 | 0.056944 | 0.71111 | 0.71969 | 0.1813
2021-10-04 | 0.36638 | 0.37029 | 4.988 | 0.056157 | 0.71359 | 0.72031 | 0.14883
2021-10-05 | 0.35308 | 0.36144 | 4.988 | 0.052235 | 0.50666 | 0.50784 | 0.26138
2021-10-06 | 0.45462 | 0.48842 | 4.988 | 0.053156 | 0.45342 | 0.44086 | 0.53318
2021-10-07 | 0.78654 | 0.78768 | 4.9879 | 0.055555 | 0.65127 | 0.64785 | 0.5298
2021-10-08 | 0.67843 | 0.67523 | 4.9879 | 0.056725 | 0.3774 | 0.36677 | 0.44439
2021-10-09 | 0.79275 | 0.804 | 4.988 | 0.058299 | 0.45343 | 0.4563 | 0.79958
2021-10-10 | 0.82135 | 0.82215 | 4.988 | 0.058324 | 0.077957 | 0.070716 | 0.73786
2021-10-11 | 0.67951 | 0.67396 | 4.9879 | 0.05863 | 0.32248 | 0.32066 | 0.74922
2021-10-12 | 0.53254 | 0.59353 | 4.988 | 0.058921 | 0.70165 | 0.71377 | 0.82426
2021-10-13 | 0.76152 | 0.81186 | 4.9879 | 0.05935 | 0.71624 | 0.72343 | 0.82349
2021-10-14 | 0.70197 | 0.578 | 4.988 | 0.059471 | 0.69017 | 0.70019 | 0.82654
2021-10-15 | 0.38179 | 1.1702 | 4.9878 | 0.059283 | 0.73468 | 0.75165 | 0.81834
2021-10-16 | 0.65153 | 0.62179 | 4.9878 | 0.059038 | 0.76134 | 0.77914 | 0.8292
2021-10-17 | 0.81092 | 0.80829 | 4.9879 | 0.058954 | 0.76168 | 0.78781 | 0.82161
2021-10-18 | 0.78319 | 0.7812 | 4.9882 | 0.058838 | 0.75028 | 0.76976 | 0.82557
2021-10-19 | 0.77422 | 0.77578 | 4.9882 | 0.058777 | 0.76854 | 0.78343 | 0.81491
2021-10-20 | 0.76425 | 0.76714 | 4.988 | 0.058934 | 0.75982 | 0.79007 | 0.82237
2021-10-21 | 0.75332 | 0.75764 | 4.9879 | 0.059007 | 0.77501 | 0.80466 | 0.81807
2021-10-22 | 0.7652 | 0.76676 | 4.9879 | 0.058957 | 0.72295 | 0.7518 | 0.82687
2021-10-23 | 0.48452 | 0.48835 | 4.9878 | 0.058922 | 0.77746 | 0.79477 | 0.83606
2021-10-24 | 0.43468 | 0.43469 | 4.988 | 0.058695 | 0.77253 | 0.79292 | 0.83203
2021-10-25 | 0.40859 | 0.40647 | 4.9881 | 0.058479 | 0.78462 | 0.79856 | 0.84231
2021-10-26 | 0.27724 | 0.28051 | 4.9882 | 0.058374 | 0.36398 | 0.36036 | 0.82553
2021-10-27 | 0.09898 | 0.097949 | 4.9867 | 0.058381 | 0.32901 | 0.33009 | 0.82214
2021-10-28 | 0.097877 | 0.097422 | 4.9884 | 0.058511 | 0.13748 | 0.12308 | 0.81477
2021-10-29 | 0.40526 | 0.41467 | 4.9884 | 0.058437 | 0.44427 | 0.41745 | 0.82691
2021-10-30 | 0.66083 | 0.65255 | 4.9884 | 0.058457 | 0.13752 | 0.12831 | 0.82312
2021-10-31 | 0.74634 | 0.74041 | 4.9886 | 0.058318 | 0.19696 | 0.18218 | 0.83619
2021-11-01 | 0.68021 | 0.66792 | 4.9885 | 0.058561 | 0.38433 | 0.37175 | 0.83263
2021-11-02 | 0.70183 | 0.70399 | 4.9882 | 0.058725 | 0.73984 | 0.74771 | 0.66764
2021-11-03 | 0.74296 | 0.73064 | 4.9879 | 0.059047 | 0.74888 | 0.77231 | 0.73327
2021-11-04 | 0.69863 | 0.6943 | 4.9877 | 0.059264 | 0.70314 | 0.71605 | 0.82656
2021-11-05 | 0.30399 | 0.28736 | 4.9877 | 0.059179 | 0.56828 | 0.57973 | 0.82163
2021-11-06 | 0.14119 | 0.1683 | 4.9876 | 0.059042 | 0.32257 | 0.31805 | 0.82357
2021-11-07 | 0.18813 | 0.16814 | 4.9877 | 0.058737 | 0.68348 | 0.68188 | 0.81601
2021-11-08 | 0.39444 | 0.32856 | 4.988 | 0.058541 | 0.34401 | 0.32317 | 0.82145
2021-11-09 | 0.72784 | 0.68156 | 4.9882 | 0.058378 | 0.75309 | 0.72895 | 0.829
2021-11-10 | 0.742 | 0.71225 | 4.9883 | 0.05834 | 0.45182 | 0.4395 | 0.82898
2021-11-11 | 0.77963 | 0.76238 | 4.9885 | 0.058326 | 0.83662 | 0.79294 | 0.79902
2021-11-12 | 0.72541 | 0.71475 | 4.9886 | 0.061042 | 0.80083 | 0.78615 | 0.83626
2021-11-13 | 0.55157 | 0.54329 | 4.9887 | 0.063527 | 0.76095 | 0.76093 | 0.83181
2021-11-14 | 0.33124 | 0.32547 | 4.9888 | 0.060554 | 0.098684 | 0.087752 | 0.83405
2021-11-15 | 0.24111 | 0.23679 | 4.9889 | 0.059594 | 0.13093 | 0.12191 | 0.82742
2021-11-16 | 0.455 | 0.44791 | 4.9887 | 0.050045 | 0.73794 | 0.74806 | 0.84183
2021-11-17 | 0.46222 | 0.45605 | 4.9884 | 0.044175 | 0.79407 | 0.75936 | 0.84506
2021-11-18 | 0.42687 | 0.42611 | 4.9883 | 0.042914 | 0.80164 | 0.77365 | 0.84317
2021-11-19 | 0.52334 | 0.5233 | 4.9883 | 0.04556 | 0.81015 | 0.79312 | 0.84114
2021-11-20 | 0.53154 | 0.52787 | 4.9884 | 0.049541 | 0.80813 | 0.78273 | 0.82719
2021-11-21 | 0.47956 | 0.48347 | 4.9883 | 0.052539 | 0.77651 | 0.78209 | 0.83043
2021-11-22 | 0.4143 | 0.41325 | 4.9885 | 0.056115 | 0.7618 | 0.75527 | 0.82002
2021-11-23 | 0.45227 | 0.44734 | 4.9884 | 0.049359 | 0.75423 | 0.75125 | 0.83285
2021-11-24 | 0.3937 | 0.39548 | 4.9884 | 0.050667 | 0.76184 | 0.75424 | 0.8416
2021-11-25 | 0.38063 | 0.37927 | 4.9884 | 0.053449 | 0.7954 | 0.76343 | 0.84426
2021-11-26 | 0.36956 | 0.36338 | 4.9887 | 0.058863 | 0.82291 | 0.75735 | 0.82577
2021-11-27 | 0.34285 | 0.34161 | 4.9888 | 0.061508 | 0.81066 | 0.75498 | 0.81728
2021-11-28 | 0.32607 | 0.32417 | 4.9887 | 0.059279 | 0.80105 | 0.76261 | 0.83151
2021-11-29 | 0.34621 | 0.34762 | 4.9887 | 0.064184 | 0.55942 | 0.52972 | 0.83126
2021-11-30 | 0.092876 | 0.08914 | 4.9887 | 0.061966 | 0.074786 | 0.051073 | 0.81702
2021-12-01 | 0.15684 | 0.15556 | 4.9886 | 0.060641 | 0.46526 | 0.42327 | 0.83079
2021-12-02 | 0.24732 | 0.24063 | 4.9886 | 0.059393 | 0.64159 | 0.72388 | 0.83889
2021-12-03 | 0.30172 | 0.29712 | 4.9888 | 0.060264 | 0.66822 | 0.70367 | 0.81969
2021-12-04 | 0.38141 | 0.38124 | 4.9888 | 0.061261 | 0.81793 | 0.7483 | 0.82348
2021-12-05 | 0.34125 | 0.34201 | 4.9891 | 0.061235 | 0.83544 | 0.74353 | 0.8151
2021-12-06 | 0.16955 | 0.16758 | 4.9891 | 0.060208 | 0.34098 | 0.29854 | 0.74275
2021-12-07 | 0.099707 | 0.09475 | 4.9891 | 0.059258 | 0.088501 | 0.066094 | 0.80622
2021-12-08 | 0.1038 | 0.10137 | 4.9893 | 0.058331 | 0.28307 | 0.264 | 0.79266
2021-12-09 | 0.10056 | 0.096897 | 4.9895 | 0.05717 | 0.050451 | 0.049769 | 0.81473
2021-12-10 | 0.07774 | 0.073468 | 4.9892 | 0.051324 | 0.056493 | 0.050366 | 0.71831
2021-12-11 | 0.081846 | 0.074852 | 4.9892 | 0.052301 | 0.063716 | 0.050417 | 0.79257
2021-12-12 | 0.085728 | 0.080733 | 4.989 | 0.054905 | 0.058311 | 0.050076 | 0.81242
2021-12-13 | 0.083798 | 0.077807 | 4.9891 | 0.05609 | 0.050366 | 0.045068 | 0.78935
2021-12-14 | 0.092428 | 0.087146 | 4.989 | 0.051657 | 0.35366 | 0.33424 | 0.84967
2021-12-15 | 0.23535 | 0.23266 | 4.9892 | 0.055064 | 0.78641 | 0.74087 | 0.80527
2021-12-16 | 0.25274 | 0.26081 | 4.989 | 0.050674 | 0.76618 | 0.73449 | 0.82339
2021-12-17 | 0.29145 | 0.29025 | 4.989 | 0.1157 | 0.83237 | 0.80149 | 0.81028
2021-12-18 | 0.30262 | 0.30017 | 4.9887 | 0.080134 | 0.84928 | 0.81797 | 0.81604
2021-12-19 | 0.31364 | 0.31327 | 4.9886 | 0.06959 | 0.86707 | 0.84376 | 0.81223
2021-12-20 | 0.34299 | 0.34782 | 4.9887 | 0.071634 | 0.87323 | 0.84865 | 0.80302
2021-12-21 | 0.39723 | 0.39478 | 4.9887 | 0.090204 | 0.89661 | 0.85696 | 0.80182
2021-12-22 | 0.38486 | 0.38357 | 4.9887 | 0.065335 | 0.87483 | 0.85885 | 0.8145
2021-12-23 | 0.38726 | 0.39303 | 4.9889 | 0.05161 | 0.56179 | 0.56308 | 0.83899
2021-12-24 | 0.18696 | 0.18696 | 4.9888 | 0.053916 | 0.49548 | 0.50077 | 0.82561
2021-12-25 | 0.43199 | 0.43272 | 4.9888 | 0.055983 | 0.84635 | 0.85665 | 0.82436
2021-12-26 | 0.32497 | 0.33107 | 4.9886 | 0.056629 | 0.84404 | 0.84576 | 0.83893
2021-12-27 | 0.39304 | 0.38082 | 4.9888 | 0.059013 | 0.83247 | 0.84291 | 0.82856
2021-12-28 | 0.37466 | 0.37035 | 4.9888 | 0.059378 | 0.83919 | 0.84525 | 0.81858
2021-12-29 | 0.13163 | 0.14213 | 4.9887 | 0.057249 | 0.39174 | 0.3861 | 0.83668
2021-12-30 | 0.36394 | 0.37085 | 4.9887 | 0.054387 | 0.84819 | 0.83981 | 0.8412
2021-12-31 | 0.36542 | 0.35934 | 4.9887 | 0.055745 | 0.84922 | 0.84693 | 0.84217
2022-01-01 | 0.29221 | 0.29431 | 4.9889 | 0.057692 | 0.86504 | 0.84691 | 0.81086
2022-01-02 | 0.29456 | 0.29564 | 4.989 | 0.060282 | 0.86628 | 0.84345 | 0.79542
2022-01-03 | 0.30316 | 0.30429 | 4.9891 | 0.061316 | 0.85767 | 0.83695 | 0.80852
2022-01-04 | 0.29059 | 0.2913 | 4.9892 | 0.063425 | 0.84762 | 0.82821 | 0.46192
2022-01-05 | 0.30046 | 0.30373 | 4.9893 | 0.064104 | 0.83841 | 0.83646 | 0.089866
2022-01-06 | 0.30781 | 0.30862 | 4.9892 | 0.063456 | 0.82902 | 0.84253 | 0.082201
2022-01-07 | 0.28505 | 0.28719 | 4.9888 | 0.061174 | 0.88042 | 0.84626 | 0.082699
2022-01-08 | 0.2733 | 0.27089 | 4.9887 | 0.060506 | 0.8938 | 0.84474 | 0.083171
2022-01-09 | 0.31099 | 0.3135 | 4.9889 | 0.063578 | 0.71979 | 0.68172 | 0.087752
2022-01-10 | 0.11414 | 0.10683 | 4.989 | 0.064762 | 0.34281 | 0.33245 | 0.087875
2022-01-11 | 0.32515 | 0.32938 | 4.9892 | 0.065069 | 0.85724 | 0.85645 | 0.085572
2022-01-12 | 0.33555 | 0.33653 | 4.9892 | 0.067772 | 0.82097 | 0.84269 | 0.088301
2022-01-13 | 0.31194 | 0.31223 | 4.9891 | 0.066827 | 0.83309 | 0.82904 | 0.083945
2022-01-14 | 0.23788 | 0.23787 | 4.9888 | 0.064231 | 0.85605 | 0.83357 | 0.084036
2022-01-15 | 0.22765 | 0.2294 | 4.9888 | 0.06405 | 0.8795 | 0.83657 | 0.086446
2022-01-16 | 0.23349 | 0.23152 | 4.9889 | 0.068006 | 0.87483 | 0.84853 | 0.083892
2022-01-17 | 0.20218 | 0.203 | 4.9891 | 0.067757 | 0.86802 | 0.85038 | 0.087366
2022-01-18 | 0.18209 | 0.18177 | 4.9893 | 0.068797 | 0.88243 | 0.85062 | 0.083429
2022-01-19 | 0.1959 | 0.19629 | 4.9894 | 0.069249 | 0.88815 | 0.84851 | 0.080642
2022-01-20 | 0.23629 | 0.24129 | 4.9893 | 0.066917 | 0.87535 | 0.85065 | 0.33118
2022-01-21 | 0.20917 | 0.21911 | 4.989 | 0.063037 | 0.84499 | 0.81554 | 0.79824
2022-01-22 | 0.19481 | 0.20078 | 4.9891 | 0.06399 | 0.78031 | 0.78981 | 0.80187
2022-01-23 | 0.20218 | 0.20776 | 4.9893 | 0.065081 | 0.78426 | 0.79409 | 0.81901
2022-01-24 | 0.18435 | 0.1874 | 4.9893 | 0.065828 | 0.78532 | 0.80305 | 0.81167
2022-01-25 | 0.19558 | 0.20016 | 4.9893 | 0.066235 | 0.78642 | 0.80463 | 0.80753
2022-01-26 | 0.18539 | 0.18966 | 4.9894 | 0.064983 | 0.79554 | 0.80595 | 0.80352
2022-01-27 | 0.19783 | 0.21162 | 4.9891 | 0.065773 | 0.80904 | 0.81213 | 0.80958
2022-01-28 | 0.16673 | 0.17046 | 4.989 | 0.064123 | 0.78595 | 0.77843 | 0.8036
2022-01-29 | 0.13428 | 0.14071 | 4.989 | 0.066256 | 0.076666 | 0.076269 | 0.80049
2022-01-30 | 0.089739 | 0.094777 | 4.9893 | 0.067143 | 0.074786 | 0.074786 | 0.81276
2022-01-31 | 0.088097 | 0.091609 | 4.9894 | 0.068221 | 0.074786 | 0.074786 | 0.78428
2022-02-01 | 0.089618 | 0.092776 | 4.9896 | 0.067627 | 0.074786 | 0.074786 | 0.79678
2022-02-02 | 0.087998 | 0.093722 | 4.9897 | 0.065928 | 0.074786 | 0.074786 | 0.80138
2022-02-03 | 0.087702 | 0.09466 | 4.9898 | 0.064918 | 0.074786 | 0.074786 | 0.79441
2022-02-04 | 0.086242 | 0.081146 | 4.9898 | 0.064503 | 0.074786 | 0.074807 | 0.81367
2022-02-05 | 0.088564 | 0.08342 | 4.9897 | 0.066177 | 0.21994 | 0.21781 | 0.80566
2022-02-06 | 0.19357 | 0.1934 | 4.9893 | 0.063757 | 0.71031 | 0.70062 | 0.80392
2022-02-07 | 0.24098 | 0.23959 | 4.989 | 0.056567 | 0.7305 | 0.72239 | 0.79776
2022-02-08 | 0.21624 | 0.21414 | 4.989 | 0.045724 | 0.75186 | 0.74481 | 0.81986
2022-02-09 | 0.17697 | 0.17538 | 4.9892 | 0.047128 | 0.76129 | 0.74664 | 0.81028
2022-02-10 | 0.1921 | 0.1894 | 4.9893 | 0.049254 | 0.74807 | 0.75092 | 0.81366
2022-02-11 | 0.22538 | 0.22478 | 4.9894 | 0.05238 | 0.74591 | 0.75672 | 0.80041
2022-02-12 | 0.1771 | 0.17383 | 4.9893 | 0.055741 | 0.67064 | 0.65991 | 0.83713
2022-02-13 | 0.085229 | 0.079156 | 4.9892 | 0.056599 | 0.11708 | 0.10926 | 0.21421
2022-02-14 | 0.089084 | 0.083636 | 4.9891 | 0.056469 | 0.35162 | 0.34818 | 0.38718
2022-02-15 | 0.21655 | 0.21616 | 4.9888 | 0.046624 | 0.73828 | 0.74718 | 0.80041
2022-02-16 | 0.18711 | 0.18637 | 4.9887 | 0.045386 | 0.53618 | 0.53623 | 0.79098
2022-02-17 | 0.25734 | 0.2568 | 4.9888 | 0.047871 | 0.77668 | 0.78204 | 0.80206
2022-02-18 | 0.26768 | 0.26824 | 4.9887 | 0.050825 | 0.74348 | 0.7466 | 0.81626
2022-02-19 | 0.30711 | 0.3066 | 4.9888 | 0.052558 | 0.78026 | 0.78841 | 0.80804
2022-02-20 | 0.26508 | 0.26258 | 4.9888 | 0.055869 | 0.76443 | 0.77359 | 0.7945
2022-02-21 | 0.24603 | 0.24275 | 4.9889 | 0.055582 | 0.75174 | 0.75942 | 0.73782
2022-02-22 | 0.25535 | 0.25652 | 4.9888 | 0.05071 | 0.75643 | 0.76541 | 0.78631
2022-02-23 | 0.24183 | 0.24179 | 4.9887 | 0.05227 | 0.76516 | 0.77215 | 0.66288
2022-02-24 | 0.27509 | 0.27398 | 4.9884 | 0.051538 | 0.78064 | 0.78277 | 0.45059
2022-02-25 | 0.33397 | 0.33607 | 4.9883 | 0.053204 | 0.80198 | 0.80059 | 0.44477
2022-02-26 | 0.28907 | 0.34357 | 4.9884 | 0.05514 | 0.80376 | 0.80138 | 0.80877
2022-02-27 | 0.28919 | 0.29494 | 4.9883 | 0.056647 | 0.78295 | 0.78406 | 0.80238
2022-02-28 | 0.28915 | 0.2885 | 4.9882 | 0.056496 | 0.74081 | 0.74571 | 0.79337